## Sheet1
AIRFOIL BLADE
SIZE D - AF - 22 | [6 empty] | DOUBLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | DOUBLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 22 ¼inches 565 mm | [13 empty] | SIZE 22 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel Circumference 5.83 feet 1.777 m | [13 empty] | CLASS I |  | 1827
Inlet Diameter / Area 24 3/16 inches Dia/6.28 sq f.t 614 mm /.5834 m² | [13 empty] | CLASS II |  | 2382
Outlet Size Area 23 5/16*31 5/16 Inches I.D/5.07 sq.ft 592*795mm/.4710m² | [13 empty] | CLASS III |  | 3002
Tip Speed 5.83* rpm ft./minute 1.777*RPM m/minute | [13 empty] | CLASS IV |  | N/A
Maximum BHP 2.27*(RPM÷1000)³ BHP 1.693* (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
3042 | 600 | 418 | 0.16 | 477 | 0.24 | 545 | 0.33
3549 | 700 | 450 | 0.21 | 501 | 0.28 | 552 | 0.37 | 610 | 0.48 | 666 | 0.59
4056 | 800 | 484 | 0.25 | 533 | 0.34 | 576 | 0.43 | 619 | 0.52 | 670 | 0.64 | 721 | 0.77 | 768 | 0.9
4563 | 900 | 520 | 0.31 | 566 | 0.41 | 607 | 0.51 | 645 | 0.6 | 683 | 0.71 | 727 | 0.83 | 772 | 0.97 | 859 | 1.27
5070 | 1000 | 558 | 0.37 | 600 | 0.48 | 640 | 0.59 | 677 | 0.7 | 711 | 0.81 | 745 | 0.92 | 781 | 1.05 | 863 | 1.36 | 942 | 1.69
5577 | 1100 | 597 | 0.44 | 635 | 0.56 | 74 | 0.68 | 710 | 0.81 | 743 | 0.93 | 775 | 1.05 | 804 | 1.17 | 891 | 1.45 | 946 | 1.79 | 1019 | 2.15
6084 | 1200 | 636 | 0.52 | 673 | 0.65 | 709 | 0.78 | 743 | 0.92 | 776 | 1.06 | 806 | 1.18 | 836 | 1.31 | 891 | 1.58 | 954 | 1.9 | 1022 | 2.26
6591 | 1300 | 676 | 0.62 | 712 | 0.76 | 754 | 0.9 | 778 | 1.04 | 809 | 1.19 | 836 | 1.34 | 868 | 1.47 | 921 | 1.76 | 973 | 2.05 | 1030 | 2.4
7098 | 1400 | 717 | 0.73 | 751 | 0.87 | 783 | 1.02 | 813 | 1.17 | 844 | 1.33 | 783 | 1.49 | 900 | 1.65 | 953 | 1.95 | 1001 | 2.26 | 1049 | 2.58
7605 | 1500 | 759 | 0.85 | 791 | 1 | 822 | 1.6 | 850 | 1.32 | 878 | 1.49 | 907 | 1.65 | 934 | 1.82 | 985 | 2.16 | 1033 | 2.48 | 1077 | 2.81
8112 | 1600 | 801 | 0.98 | 832 | 1.15 | 861 | 1.32 | 889 | 1.49 | 915 | 1.66 | 942 | 1.84 | 968 | 2.01 | 1018 | 2.38 | 1065 | 2.73 | 1109 | 3.07
8619 | 1700 | 844 | 1.14 | 872 | 1.31 | 901 | 1.49 | 928 | 1.67 | 953 | 1.85 | 978 | 2.03 | 1003 | 2.22 | 1052 | 2.6 | 1097 | 2.99 | 1141 | 3.35
9126 | 1800 | 887 | 1.3 | 914 | 1.49 | 941 | 1.68 | 967 | 1.86 | 992 | 2.05 | 1016 | 2.25 | 1039 | 2.44 | 1086 | 2.84 | 1131 | 3.25 | 1173 | 3.66
9633 | 1900 | 930 | 1.49 | 956 | 1.68 | 981 | 1.88 | 1007 | 2.08 | 1031 | 2.28 | 1054 | 2.48 | 1076 | 2.68 | 1121 | 3.1 | 1165 | 3.52 | 1206 | 3.96
10140 | 2000 | 974 | 1.69 | 999 | 1.9 | 1022 | 2.11 | 1047 | 2.31 | 1070 | 2.52 | 1093 | 2.73 | 1115 | 2.94 | 1156 | 3.38 | 1199 | 3.82 | 1240 | 4.27
11154 | 2200 | 1061 | 2.16 | 1084 | 2.38 | 1107 | 2.61 | 1128 | 2.84 | 1150 | 3.06 | 1172 | 3.29 | 1192 | 3.52 | 1232 | 3.99 | 1270 | 4.47 | 1309 | 4.95
12168 | 2400 | 1149 | 2.71 | 1171 | 2.95 | 1192 | 3.2 | 1212 | 3.45 | 1232 | 3.7 | 1252 | 3.94 | 1272 | 4.19 | 1310 | 4.69 | 1346 | 5.2 | 1380 | 5.73
13182 | 2600 | 1238 | 3.35 | 1258 | 3.62 | 1278 | 3.88 | 1297 | 4.15 | 1315 | 4.42 | 1333 | 4.69 | 1352 | 4.95 | 1388 | 5.49 | 1423 | 6.04 | 1456 | 6.59
14196 | 2800 | 1327 | 4.1 | 1346 | 4.38 | 1364 | 4.66 | 1382 | 4.95 | 1400 | 5.24 | 1417 | 5.3 | 1433 | 5.82 | 1468 | 6.39 | 1501 | 6.97 | 1533 | 7.56
15210 | 3000 | 1417 | 4.96 | 1434 | 5.25 | 1452 | 5.55 | 1469 | 5.86 | 1485 | 6.17 | 1501 | 6.47 | 1517 | 6.79 | 1549 | 7.41 | 1581 | 8.02 | 1612 | 8.64
16224 | 3200 | 1506 | 5.93 | 1523 | 6.24 | 1539 | 6.56 | 1556 | 6.89 | 1571 | 7.21 | 1587 | 7.54 | 1602 | 7.87 | 1631 | 8.53 | 1662 | 9.19 | 1691 | 9.85
17238 | 3400 | 1596 | 7.02 | 1612 | 7.36 | 1628 | 7.7 | 1643 | 8.04 | 1658 | 8.38 | 1673 | 8.73 | 1687 | 9.07 | 1715 | 9.78 | 1743 | 10.49 | 1771 | 11.18
18252 | 3600 | 1687 | 8.25 | 1702 | 8.6 | 1716 | 8.96 | 1731 | 9.32 | 1745 | 9.68 | 1759 | 10.05 | 1773 | 10.41 | 1800 | 11.15 | 1826 | 11.9 | 1853 | 12.64
19266 | 3800 | 1777 | 9.62 | 1791 | 9.99 | 1805 | 10.37 | 1819 | 10.74 | 1833 | 11.12 | 1846 | 11.51 | 1859 | 11.89 | 1885 | 12.67 | 1911 | 13.45 | 1935 | 14.24
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
6084 | 1200 | 1090 | 2.66
6591 | 1300 | 1092 | 2.79 | 1217 | 3.65
7098 | 1400 | 1102 | 2.94 | 1220 | 3.81 | 1330 | 4.72
7605 | 1500 | 1122 | 3.16 | 1226 | 3.98 | 1335 | 4.94 | 1435 | 5.91
8112 | 1600 | 1150 | 3.42 | 1236 | 4.18 | 1338 | 5.13 | 1441 | 6.18 | 1533 | 7.2
8619 | 1700 | 1182 | 3.72 | 1260 | 4.48 | 1348 | 5.37 | 1444 | 6.4 | 1540 | 7.52 | 1626 | 8.6
9126 | 1800 | 1214 | 4.04 | 1289 | 4.82 | 1365 | 5.66 | 1452 | 6.66 | 1543 | 7.77 | 1633 | 8.96 | 1715 | 10.11
9633 | 1900 | 1246 | 4.38 | 1321 | 5.19 | 1390 | 6.03 | 1464 | 6.95 | 1549 | 8.06 | 1636 | 9.24 | 1721 | 10.49 | 1800 | 11.73
10140 | 2000 | 1279 | 4.73 | 1353 | 5.59 | 1421 | 6.46 | 1487 | 7.37 | 1560 | 8.38 | 1642 | 9.56 | 1724 | 10.81 | 1805 | 12.13 | 1881 | 13.45 | 1948 | 14.65
11154 | 2200 | 1347 | 5.44 | 1418 | 6.45 | 1484 | 7.39 | 1547 | 8.34 | 1605 | 9.31 | 1669 | 10.37 | 1739 | 11.55 | 1813 | 12.86 | 1888 | 14.24 | 1962 | 15.68
12168 | 2400 | 1416 | 6.25 | 1485 | 7.33 | 1549 | 8.43 | 1610 | 9.44 | 1668 | 10.47 | 1723 | 11.52 | 1779 | 12.62 | 1837 | 13.79 | 1903 | 15.13 | 1971 | 16.55
13182 | 2600 | 1488 | 7.16 | 1554 | 8.3 | 1616 | 9.46 | 1675 | 10.66 | 1732 | 11.76 | 1786 | 12.87 | 1838 | 14 | 1887 | 15.14 | 1940 | 16.36 | 1994 | 17.63
14196 | 2800 | 1564 | 8.16 | 1623 | 9.38 | 1685 | 10.61 | 1742 | 11.87 | 1797 | 13.15 | 1850 | 14.35 | 1901 | 15.54 | 1950 | 16.74 | 1997 | 17.96 | 2042 | 19.2
15210 | 3000 | 1642 | 9.27 | 1698 | 10.56 | 1754 | 11.87 | 1811 | 13.19 | 1864 | 14.54 | 1915 | 15.91 | 1965 | 17.21 | 2013 | 18.48 | 2060 | 19.76 | 2104 | 21.06
16224 | 3200 | 1720 | 10.51 | 1775 | 11.86 | 1827 | 13.24 | 1880 | 14.64 | 1932 | 16.05 | 1983 | 17.49 | 2031 | 18.95 | 2078 | 20.37 | 2123 | 21.72 | 2168 | 23.07
17238 | 3400 | 1799 | 11.87 | 1852 | 13.29 | 1903 | 14.74 | 1952 | 16.21 | 2002 | 17.69 | 2051 | 19.19 | 2098 | 20.72 | 2144 | 22.26 | 2188 | 23.82 | 2232 | 25.24
18252 | 3600 | 1879 | 13.37 | 1931 | 14.86 | 1980 | 16.37 | 2027 | 17.91 | 2073 | 19.47 | 2120 | 21.04 | 2167 | 22.63 | 2212 | 24.23 | 2255 | 25.86 | 2297 | 27.51
19266 | 3800 | 1960 | 15.02 | 2010 | 16.57 | 2058 | 18.15 | 2104 | 19.75 | 2148 | 21.38 | 2191 | 23.03 | 2236 | 24.69 | 2280 | 26.36 | 2323 | 28.05 | 2364 | 29.75
20280 | 4000 | 2042 | 16.81 | 2090 | 18.44 | 2137 | 20.08 | 2181 | 21.75 | 2224 | 23.44 | 2266 | 25.16 | 2306 | 26.9 | 2349 | 28.63 | 2391 | 30.39 | 2432 | 32.16
21294 | 4200 | 2126 | 18.73 | 2171 | 20.46 | 2216 | 22.17 | 2259 | 23.91 | 2301 | 25.67 | 2342 | 27.45 | 2381 | 29.25 | 2420 | 31.07 | 2461 | 32.89 | 2501 | 34.73
22308 | 4400 | 2210 | 20.82 | 2253 | 22.65 | 2296 | 24.43 | 2338 | 26.23 | 2379 | 28.06 | 2419 | 29.9 | 2457 | 31.77 | 2495 | 33.66 | 2531 | 35.57 | 2570 | 37.47
23322 | 4600 | 2295 | 23.08 | 2336 | 24.98 | 2377 | 26.86 | 2418 | 28.73 | 2458 | 30.62 | 2497 | 32.54 | 2534 | 34.47 | 2571 | 36.42 | 2606 | 38.39 | 2641 | 40.38
24336 | 4800 | 2380 | 25.52 | 2420 | 27.49 | 2458 | 29.48 | 2498 | 31.42 | 2537 | 33.37 | 2575 | 35.35 | 2612 | 37.35 | 2647 | 39.37 | 2682 | 41.4 | 2716 | 43.45
25350 | 5000 | 2466 | 28.14 | 2504 | 30.19 | 2541 | 32.26 | 2579 | 34.29 | 2617 | 36.32 | 2654 | 38.36 | 2690 | 40.42 | 2725 | 42.50 | 2759 | 44.60 | 2792 | 46.72
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
11154 | 2200 | 2034 | 17.15
12168 | 2400 | 2039 | 18.04 | 2174 | 21.18 | 2295 | 24.22
13182 | 2600 | 2056 | 19.09 | 2179 | 22.2 | 2307 | 25.57 | 2426 | 29.02
14196 | 2800 | 2093 | 20.53 | 2199 | 23.44 | 2314 | 26.75 | 2432 | 30.31 | 2546 | 33.99 | 2650 | 37.54
15210 | 3000 | 2148 | 22.37 | 2237 | 25..13 | 2334 | 28.16 | 2443 | 31.69 | 2551 | 35.39 | 2660 | 39.28 | 2765 | 43.25 | 2857 | 46.91
16224 | 3200 | 2210 | 24.44 | 2292 | 27.22 | 2376 | 30.15 | 2463 | 33.26 | 2566 | 36.99 | 2665 | 40.8 | 2770 | 44.9 | 2870 | 49.07 | 2967 | 53.33
17238 | 3400 | 2274 | 26.68 | 2355 | 29.58 | 2432 | 32.52 | 2510 | 35.6 | 2591 | 38.88 | 2685 | 42.66 | 2779 | 46.66 | 2875 | 50.85 | 2972 | 55.22
18252 | 3600 | 2339 | 29.07 | 2418 | 32.1 | 2494 | 35.17 | 2567 | 38.28 | 2639 | 41.49 | 2717 | 44.94 | 2799 | 48.69 | 2890 | 52.88 | 2977 | 57.15
19266 | 3800 | 2405 | 31.48 | 2483 | 34.8 | 2558 | 37.99 | 2629 | 41.23 | 2698 | 44.5 | 2764 | 47.82 | 2838 | 51.44 | 2910 | 55.1 | 2997 | 59.47
20280 | 4000 | 2472 | 33.95 | 2548 | 37.58 | 2622 | 41 | 2692 | 44.36 | 2760 | 47.76 | 2826 | 51.19 | 2889 | 54.66 | 2957 | 58.37
21294 | 4200 | 2540 | 36.58 | 2615 | 40.34 | 2687 | 44.16 | 2757 | 47.69 | 2824 | 51.21 | 2888 | 54.77 | 2951 | 58.36
22308 | 4400 | 2609 | 39.39 | 2683 | 43.27 | 2753 | 47.21 | 2821 | 51.22 | 2888 | 54.87 | 2952 | 58.55
23322 | 4600 | 2678 | 42.37 | 2751 | 46.38 | 2821 | 50.45 | 2888 | 54.58 | 2952 | 58.74
24336 | 4800 | 2750 | 45.53 | 2820 | 49.67 | 2889 | 53.87 | 2955 | 58.12