## Sheet1
AIRFOIL BLADE
SIZE D - AF - 73 | [6 empty] | DOUBLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | DOUBLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 73 inches 1854mm | [13 empty] | SIZE 73 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel Circumference 19.1 feet 5.822 m | [13 empty] | CLASS I |  | 556
Inlet Diameter / Area 82 3/8 inches Dia/72.6 sq f.t 2092mm /6.745m² | [13 empty] | CLASS II |  | 724
Outlet Size Area 76 15/16* 103 7/8 Inches I.D/55.5 sq.ft 1954*2638 mm/5.156 m² | [13 empty] | CLASS III |  | 913
Tip Speed 19.1* rpm ft./minute 5.822*RPM m/minute | [13 empty] | CLASS IV |  | N/A
Maximum BHP 862.50*(RPM÷1000)³ BHP 643.2* (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
33300 | 600 | 127 | 1.75 | 144 | 2.47
38850 | 700 | 137 | 2.19 | 152 | 3 | 167 | 3.85 | 182 | 4.8
44400 | 800 | 147 | 2.65 | 162 | 3.62 | 175 | 4.56 | 188 | 5.53 | 200 | 6.57
49950 | 900 | 157 | 3.21 | 171 | 4.3 | 185 | 5.37 | 196 | 6.42 | 208 | 7.51 | 218 | 8.62 | 230 | 9.87
55500 | 1000 | 169 | 3.88 | 182 | 5.01 | 194 | 6.27 | 206 | 7.43 | 216 | 8.6 | 227 | 9.8 | 237 | 11.03 | 257 | 13.71
61050 | 1100 | 181 | 4.67 | 193 | 5.87 | 204 | 7.18 | 215 | 8.57 | 226 | 9.83 | 236 | 11.11 | 245 | 12.42 | 263 | 15.11 | 282 | 18.08
66600 | 1200 | 193 | 5.59 | 204 | 6.87 | 214 | 8.2 | 225 | 9.68 | 235 | 11.2 | 245 | 12.57 | 254 | 13.96 | 271 | 16.81 | 288 | 19.76 | 305 | 23
72150 | 1300 | 205 | 6.61 | 216 | 8 | 226 | 9.41 | 235 | 10.9 | 245 | 12.52 | 254 | 14.17 | 263 | 15.65 | 280 | 16.68 | 296 | 21.79 | 311 | 24.99
77700 | 1400 | 218 | 7.75 | 228 | 9.28 | 237 | 10.78 | 246 | 12.32 | 255 | 13.96 | 264 | 15.71 | 273 | 17.5 | 289 | 20.71 | 305 | 23.99 | 319 | 27.35
83250 | 1500 | 231 | 9.04 | 240 | 10.71 | 249 | 12.3 | 258 | 13.92 | 266 | 15.58 | 274 | 17.38 | 283 | 19.25 | 299 | 22.92 | 314 | 26.37 | 328 | 29.89
88800 | 1600 | 243 | 10.48 | 253 | 12.27 | 261 | 13.99 | 270 | 15.7 | 277 | 17.44 | 285 | 19.22 | 293 | 21.16 | 309 | 25.18 | 323 | 28.95 | 337 | 32.64
94350 | 1700 | 256 | 12.08 | 265 | 13.97 | 273 | 15.85 | 281 | 17.65 | 289 | 19.48 | 296 | 21.34 | 303 | 23.23 | 319 | 27.42 | 333 | 31.73 | 346 | 35.6
99900 | 1800 | 269 | 13.87 | 278 | 15.85 | 286 | 17.8 | 293 | 19.79 | 301 | 21.71 | 308 | 23.65 | 315 | 25.63 | 329 | 29.84 | 343 | 34.34 | 356 | 38.77
105450 | 1900 | 282 | 15.84 | 290 | 17.92 | 298 | 20.04 | 306 | 22.13 | 313 | 24.14 | 320 | 26.17 | 326 | 28.23 | 339 | 32.44 | 353 | 37.11 | 366 | 41.9
111000 | 2000 | 295 | 18 | 303 | 20.18 | 311 | 22.4 | 318 | 24.66 | 325 | 26.78 | 332 | 28.9 | 338 | 31.05 | 350 | 35.42 | 363 | 40.06 | 376 | 45.03
122100 | 2200 | 322 | 22.97 | 329 | 25.34 | 336 | 27.76 | 343 | 30.21 | 349 | 32.7 | 356 | 35.03 | 362 | 37.35 | 374 | 42.07 | 385 | 46.89 | 396 | 51.9
133200 | 2400 | 348 | 28.84 | 355 | 31.42 | 362 | 34.02 | 368 | 36.67 | 374 | 39.35 | 380 | 42.06 | 386 | 44.64 | 397 | 49.71 | 408 | 54.86 | 418 | 60.11
144300 | 2600 | 375 | 35.71 | 381 | 38.48 | 387 | 41.29 | 393 | 44.12 | 399 | 46.99 | 405 | 49.89 | 411 | 52.82 | 421 | 58.41 | 432 | 63.91 | 442 | 69.49
155400 | 2800 | 402 | 43.65 | 408 | 46.62 | 414 | 49.62 | 419 | 52.66 | 425 | 55.72 | 430 | 58.81 | 436 | 61.93 | 446 | 68.26 | 456 | 74.11 | 465 | 80.04
166500 | 3000 | 429 | 52.75 | 434 | 55.92 | 440 | 59.12 | 445 | 62.35 | 451 | 65.6 | 456 | 68.89 | 461 | 72.2 | 471 | 78.9 | 480 | 85.56 | 489 | 91.83
177600 | 3200 | 456 | 63.08 | 461 | 66.46 | 466 | 69.85 | 471 | 73.28 | 476 | 76.73 | 481 | 80.21 | 486 | 83.71 | 496 | 90.8 | 505 | 97.98 | 513 | 104.96
188700 | 3400 | 483 | 74.74 | 488 | 78.31 | 493 | 81.91 | 498 | 85.53 | 503 | 89.18 | 507 | 92.85 | 512 | 96.55 | 521 | 104.02 | 529 | 111.58 | 538 | 119.23
199800 | 3600 | 510 | 87.81 | 515 | 91.58 | 520 | 95.37 | 524 | 99.19 | 529 | 103.04 | 533 | 106.91 | 538 | 110.8 | 546 | 118.65 | 555 | 126.59 | 563 | 134.62
210900 | 3800 | 537 | 102.36 | 542 | 106.33 | 547 | 110.32 | 551 | 114.34 | 555 | 118.38 | 560 | 122.45 | 564 | 126.53 | 572 | 134.77 | 580 | 143.09 | 588 | 151.5
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
72150 | 1300 | 327 | 28.45
77700 | 1400 | 333 | 30.79 | 363 | 38.36
83250 | 1500 | 342 | 33.5 | 368 | 40.97 | 396 | 49.38
88800 | 1600 | 350 | 36.41 | 375 | 44.16 | 400 | 52.47
94350 | 1700 | 359 | 39.53 | 384 | 47.6 | 407 | 55.93 | 431 | 65.06
99900 | 1800 | 369 | 42.88 | 392 | 51.28 | 415 | 59.94 | 436 | 68.82 | 460 | 78.74
105450 | 1900 | 378 | 46.45 | 402 | 55.2 | 423 | 64.17 | 444 | 73.4 | 465 | 82.93 | 487 | 93.49
111000 | 2000 | 388 | 50.11 | 411 | 59.36 | 432 | 68.67 | 453 | 78.21 | 472 | 87.97 | 492 | 98.19 | 513 | 109.31
122100 | 2200 | 408 | 57.33 | 430 | 68.45 | 451 | 78.46 | 470 | 88.65 | 489 | 99.05 | 507 | 109.68 | 525 | 120.47 | 543 | 131.92 | 562 | 144.14
133200 | 2400 | 428 | 65.44 | 450 | 77.27 | 470 | 89.36 | 489 | 100.25 | 507 | 111.32 | 524 | 122.56 | 541 | 134.02 | 558 | 145.65 | 574 | 157.44 | 591 | 169.91
144300 | 2600 | 451 | 75.16 | 470 | 87.02 | 490 | 99.91 | 508 | 113.06 | 526 | 124.82 | 543 | 136.75 | 559 | 148.83 | 575 | 161.09 | 590 | 173.55 | 606 | 186.16
155400 | 2800 | 474 | 86.05 | 492 | 98.29 | 510 | 111.4 | 528 | 125.31 | 545 | 139.53 | 562 | 152.25 | 577 | 165.03 | 593 | 177.95 | 608 | 191.01 | 622 | 204.26
166500 | 3000 | 498 | 98.18 | 515 | 111.1 | 531 | 124.3 | 548 | 138.6 | 565 | 153.5 | 581 | 168.7 | 596 | 182.63 | 611 | 196.24 | 626 | 209.98 | 640 | 223.87
177600 | 3200 | 522 | 111.65 | 538 | 125.25 | 554 | 139.12 | 569 | 153.25 | 585 | 168.68 | 600 | 184.55 | 616 | 200.69 | 630 | 216.05 | 645 | 230.48 | 659 | 245.04
188700 | 3400 | 546 | 126.54 | 562 | 140.83 | 577 | 155.37 | 591 | 170.16 | 605 | 185.19 | 621 | 201.69 | 635 | 218.5 | 650 | 235.57 | 664 | 252.58 | 677 | 267.83
199800 | 3600 | 571 | 142.74 | 586 | 157.91 | 601 | 173.14 | 615 | 188.6 | 628 | 204.29 | 641 | 220.2 | 656 | 237.68 | 670 | 255.42 | 683 | 273.41 | 696 | 291.64
210900 | 3800 | 595 | 159.99 | 610 | 176.59 | 624 | 192.5 | 638 | 208.63 | 651 | 224.99 | 664 | 241.56 | 676 | 258.35 | 690 | 276.72 | 703 | 295.38 | 716 | 314.27
222000 | 4000 | 620 | 178.82 | 635 | 196.78 | 648 | 213.55 | 662 | 230.36 | 674 | 247.39 | 687 | 264.62 | 699 | 282.06 | 711 | 299.7 | 723 | 318.87 | 736 | 338.43
233100 | 4200 | 646 | 199.3 | 659 | 218.01 | 673 | 236.36 | 686 | 253.86 | 698 | 271.56 | 710 | 289.46 | 722 | 307.56 | 733 | 325.85 | 744 | 344.33 | 756 | 364.18
244200 | 4400 | 671 | 221.53 | 684 | 240.99 | 697 | 260.73 | 710 | 279.22 | 722 | 297.6 | 734 | 316.17 | 745 | 334.93 | 756 | 353.88 | 767 | 373.01 | 778 | 392.32
255300 | 4600 | 696 | 245.57 | 709 | 265.78 | 722 | 286.26 | 734 | 306.51 | 746 | 325.58 | 757 | 344.83 | 769 | 364.26 | 779 | 383.86 | 790 | 403.65 | 800 | 423.6
266400 | 4800 | 722 | 271.51 | 735 | 292.48 | 747 | 313.7 | 759 | 335.18 | 770 | 355.59 | 781 | 375.51 | 792 | 395.61 | 803 | 415.89 | 813 | 436.33 | 823 | 456.94
277500 | 5000 | 748 | 299.44 | 760 | 321.16 | 772 | 343.13 | 783 | 365.34 | 794 | 387.71 | 805 | 408.32 | 816 | 429.09 | 826 | 450.03 | 837 | 471.13 | 847 | 492.4
288600 | 5200 | 774 | 329.42 | 786 | 351.9 | 797 | 374.61 | 808 | 397.57 | 819 | 420.76 | 830 | 443.32 | 840 | 464.77 | 850 | 486.38 | 860 | 508.15 | 870 | 530.07
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
133200 | 2400 | 608 | 183.19
144300 | 2600 | 620 | 198.9 | 652 | 226.47 | 683 | 255.54
155400 | 2800 | 637 | 217.68 | 664 | 244.9 | 693 | 273.97 | 723 | 305.02
166500 | 3000 | 654 | 237.88 | 681 | 266.43 | 707 | 295.49 | 732 | 325.71 | 761 | 385.7
177600 | 3200 | 672 | 259.73 | 698 | 289.49 | 723 | 319.86 | 747 | 350.72 | 771 | 382.02 | 797 | 416.59 | 823 | 451.97
188700 | 3400 | 691 | 283.2 | 716 | 314.3 | 740 | 345.87 | 764 | 378.03 | 787 | 410.65 | 809 | 443.68 | 833 | 478.73 | 858 | 515.96 | 882 | 553.62
199800 | 3600 | 709 | 308.37 | 735 | 340.83 | 758 | 373.74 | 781 | 407.09 | 804 | 440.99 | 826 | 475.34 | 847 | 510.08 | 867 | 545.2 | 891 | 584.18
210900 | 3800 | 729 | 333.39 | 753 | 369.18 | 777 | 403.43 | 799 | 438.11 | 821 | 473.2 | 842 | 508.79 | 863 | 544.85 | 883 | 619.25 | 903 | 618.05
222000 | 4000 | 749 | 358.21 | 772 | 398.42 | 796 | 435.04 | 818 | 471.06 | 839 | 507.47 | 860 | 544.27 | 880 | 581.51 | 900
233100 | 4200 | 769 | 384.64 | 792 | 426.17 | 815 | 468.5 | 837 | 506.01 | 858 | 543.76 | 878 | 581.88 | 898 | 620.36
244200 | 4400 | 789 | 412.73 | 812 | 455.6 | 834 | 499.25 | 855 | 543.05 | 876 | 582.15 | 896 | 621.6
255300 | 4600 | 811 | 443.73 | 832 | 486.79 | 854 | 531.76 | 875 | 577.47 | 895 | 622.72
266400 | 4800 | 833 | 477.71 | 853 | 519.79 | 874 | 566.1 | 895 | 613.13
277500 | 5000 | 856 | 513.82 | 875 | 557.14 | 894 | 602.34