## Sheet1
AIRFOIL BLADE
SIZE S - AF - 20 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 20 inches 508 mm | [13 empty] | SIZE 20 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 5.24 feet 1.597 m | [13 empty] | CLASS I |  | 2183
Inlet Diameter / Area 21 15/16 inches Dia/2.58 sq f.t 557mm /.2397 m² | [13 empty] | CLASS II |  | 2848
Outlet Size Area 21 *15 13/16Inches I.D/2.32 sq.ft 533*402mm/.2155 m² | [13 empty] | CLASS III |  | 3588
Tip Speed 5.24 * rpm ft./minute 1.597*RPM m/minute | [13 empty] | CLASS IV |  | 3947
Maximum BHP .67*(RPM÷1000)³ BHP .4996 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
1392 | 600 | 506 | 0.08 | 566 | 0.12 | 622 | 0.15 | 674 | 0.19
1624 | 700 | 550 | 0.11 | 605 | 0.14 | 656 | 0.18 | 704 | 0.22 | 751 | 0.26 | 795 | 0.3 | 839 | 0.35
1856 | 800 | 597 | 0.13 | 647 | 0.17 | 696 | 0.22 | 740 | 0.26 | 781 | 0.31 | 824 | 0.35 | 865 | 0.4 | 939 | 0.49
2088 | 900 | 646 | 0.16 | 693 | 0.21 | 736 | 0.26 | 780 | 0.31 | 820 | 0.36 | 858 | 0.41 | 894 | 0.46 | 968 | 0.56 | 1036 | 0.66
2320 | 1000 | 695 | 0.2 | 741 | 0.25 | 782 | 0.3 | 821 | 0.36 | 860 | 0.41 | 897 | 0.47 | 931 | 0.52 | 998 | 0.64 | 1065 | 0.75 | 1126 | 0.86
2552 | 1100 | 746 | 0.24 | 790 | 0.3 | 829 | 0.36 | 866 | 0.41 | 901 | 0.47 | 937 | 0.53 | 971 | 0.59 | 1034 | 0.72 | 1094 | 0.84 | 1156 | 0.96
2784 | 1200 | 797 | 0.29 | 839 | 0.35 | 877 | 0.42 | 913 | 0.48 | 946 | 0.54 | 978 | 0.61 | 1011 | 0.67 | 1074 | 0.8 | 1131 | 0.94 | 1185 | 1.07
3016 | 1300 | 850 | 0.34 | 889 | 0.41 | 926 | 0.48 | 961 | 0.55 | 993 | 0.62 | 1024 | 0.68 | 1053 | 0.75 | 1114 | 0.89 | 1170 | 1.04 | 1223 | 1.18
3248 | 1400 | 903 | 0.41 | 941 | 0.48 | 976 | 0.55 | 1009 | 0.63 | 1041 | 0.7 | 1071 | 0.77 | 1099 | 0.85 | 1154 | 1 | 1210 | 1.15 | 1262 | 1.3
3480 | 1500 | 956 | 0.48 | 992 | 0.55 | 1026 | 0.63 | 1059 | 0.71 | 1089 | 0.79 | 1118 | 0.87 | 1146 | 0.95 | 1199 | 1.11 | 1251 | 1.27 | 1302 | 1.43
3712 | 1600 | 1010 | 0.56 | 1045 | 0.64 | 1077 | 0.72 | 1109 | 0.8 | 1138 | 0.89 | 1167 | 0.98 | 1194 | 1.06 | 1245 | 1.23 | 1293 | 1.4 | 1342 | 1.57
3944 | 1700 | 1065 | 0.65 | 1098 | 0.73 | 1129 | 0.82 | 1159 | 0.91 | 1188 | 1 | 1215 | 1.09 | 1242 | 1.18 | 1292 | 1.36 | 1339 | 1.53 | 1384 | 1.72
4176 | 1800 | 1120 | 0.75 | 1151 | 0.84 | 1181 | 0.93 | 1210 | 1.02 | 1238 | 1.11 | 1265 | 1.21 | 1291 | 1.31 | 1340 | 1.5 | 1386 | 1.68 | 1429 | 1.87
4408 | 1900 | 1175 | 0.85 | 1205 | 0.95 | 1234 | 1.05 | 1262 | 1.14 | 1289 | 1.24 | 1315 | 1.34 | 1340 | 1.44 | 1388 | 1.65 | 1433 | 1.84 | 1476 | 2.04
4640 | 2000 | 1231 | 0.97 | 1259 | 1.08 | 1287 | 1.18 | 1314 | 1.28 | 1340 | 1.38 | 1365 | 1.49 | 1390 | 1.59 | 1437 | 1.81 | 1481 | 2.02 | 1523 | 2.22
5104 | 2200 | 1343 | 1.25 | 1369 | 1.36 | 1394 | 1.48 | 1420 | 1.59 | 1444 | 1.7 | 1468 | 1.81 | 1491 | 1.92 | 1536 | 2.15 | 1578 | 2.39 | 1618 | 2.62
5568 | 2400 | 1455 | 1.57 | 1480 | 1.7 | 1503 | 1.82 | 1526 | 1.94 | 1550 | 2.06 | 1572 | 2.19 | 1594 | 2.31 | 1636 | 2.56 | 1677 | 2.81 | 1716 | 3.07
6032 | 2600 | 1569 | 1.95 | 1591 | 2.08 | 1613 | 2.22 | 1635 | 2.36 | 1656 | 2.49 | 1678 | 2.62 | 1699 | 2.75 | 1739 | 3.02 | 1778 | 3.29 | 1815 | 3.56
6496 | 2800 | 1683 | 2.39 | 1704 | 2.53 | 1724 | 2.68 | 1744 | 2.83 | 1764 | 2.98 | 1785 | 3.11 | 1804 | 3.25 | 1843 | 3.54 | 1880 | 3.82 | 1915 | 4.11
6960 | 3000 | 1797 | 2.89 | 1817 | 3.05 | 1836 | 3.2 | 1855 | 3.36 | 1874 | 3.52 | 1892 | 3.68 | 1911 | 3.82 | 1948 | 4.12 | 1983 | 4.43 | 2018 | 4.74
7424 | 3200 | 1911 | 3.46 | 1930 | 3.63 | 1948 | 3.8 | 1966 | 3.96 | 1984 | 4.13 | 2002 | 4.3 | 2019 | 4.47 | 2054 | 4.78 | 2088 | 5.11 | 2121 | 5.43
7888 | 3400 | 2026 | 4.11 | 2044 | 4.29 | 2061 | 4.46 | 2078 | 4.64 | 2095 | 4.82 | 2112 | 4.99 | 2128 | 5.17 | 2161 | 5.52 | 2194 | 5.86 | 2225 | 6.2
8352 | 3600 | 2141 | 4.84 | 2158 | 5.02 | 2175 | 5.2 | 2191 | 5.39 | 2207 | 5.58 | 2223 | 5.77 | 2238 | 5.96 | 2269 | 6.33 | 2300 | 6.69 | 2331 | 7.05
8816 | 3800 | 2257 | 5.64 | 2273 | 5.84 | 2288 | 6.03 | 2304 | 6.23 | 2319 | 6.42 | 2334 | 6.62 | 2349 | 6.82 | 2378 | 7.22 | 2408 | 7.61 | 2437 | 7.99
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
3016 | 1300 | 1273 | 1.33 | 1376 | 1.62 | 1471 | 1.92
3248 | 1400 | 1311 | 1.46 | 1406 | 1.78 | 1500 | 2.09 | 1588 | 2.41 | 1675 | 2.77
3480 | 1500 | 1350 | 1.6 | 1440 | 1.94 | 1530 | 2.27 | 1617 | 2.61 | 1698 | 2.95 | 1778 | 3.32
3712 | 1600 | 1390 | 1.74 | 1479 | 2.1 | 1561 | 2.46 | 1646 | 2.82 | 1727 | 3.18 | 1803 | 3.54 | 1875 | 3.91
3944 | 1700 | 1431 | 1.9 | 1518 | 2.27 | 159 | 2.65 | 1676 | 3.04 | 1756 | 3.42 | 1832 | 3.8 | 1904 | 4.18 | 1972 | 4.57
4176 | 1800 | 1472 | 2.07 | 1558 | 2.45 | 1638 | 2.85 | 1713 | 3.26 | 1786 | 3.67 | 1861 | 4.07 | 1933 | 4.47 | 2001 | 4.88 | 2067 | 5.29 | 2134 | 5.76
4408 | 1900 | 1517 | 2.24 | 1599 | 2.65 | 1678 | 3.06 | 1752 | 3.49 | 1821 | 3.92 | 1891 | 4.35 | 1962 | 4.77 | 2030 | 5.19 | 2095 | 5.62 | 2158 | 6.05
4640 | 2000 | 1563 | 2.43 | 1640 | 2.86 | 1718 | 3.29 | 1791 | 3.73 | 1860 | 4.17 | 1925 | 4.63 | 1992 | 5.08 | 2060 | 5.52 | 2124 | 5.97 | 2187 | 6.42
5104 | 2200 | 1657 | 2.85 | 1730 | 3.31 | 1799 | 3.78 | 1871 | 4.25 | 1938 | 4.73 | 2003 | 5.22 | 2064 | 5.71 | 2123 | 6.22 | 2184 | 6.71 | 2245 | 7.19
5568 | 2400 | 1753 | 3.33 | 1824 | 3.82 | 1890 | 4.32 | 1953 | 4.83 | 2019 | 5.34 | 2082 | 5.86 | 2142 | 6.39 | 2200 | 6.92 | 2256 | 7.46 | 2310 | 8.01
6032 | 2600 | 1851 | 3.84 | 1919 | 4.39 | 1983 | 4.92 | 2044 | 5.46 | 2103 | 6.02 | 2163 | 6.57 | 2222 | 7.13 | 2279 | 7.69 | 2334 | 8.27 | 2387 | 8.84
6496 | 2800 | 1950 | 4.41 | 2016 | 5.01 | 2079 | 5.59 | 2138 | 6.17 | 2194 | 6.75 | 2249 | 7.35 | 2304 | 7.94 | 2360 | 8.54 | 2414 | 9.14 | 2466 | 9.75
6960 | 3000 | 2051 | 5.05 | 2115 | 5.68 | 2175 | 6.33 | 2233 | 6.94 | 2288 | 7.56 | 2341 | 8.18 | 2392 | 8.82 | 2441 | 9.46 | 2494 | 10.09 | 2546 | 10.73
7424 | 3200 | 2153 | 5.76 | 2214 | 6.42 | 2273 | 7.1 | 2329 | 7.79 | 2383 | 8.44 | 2434 | 9.1 | 2484 | 9.76 | 2532 | 10.44 | 2579 | 11.12 | 2627 | 11.8
7888 | 3400 | 2256 | 6.55 | 2315 | 7.25 | 2372 | 7.96 | 2427 | 8.68 | 2479 | 9.42 | 2529 | 10.1 | 2578 | 10.8 | 2625 | 11.5 | 2671 | 12.21 | 2715 | 12.93
8352 | 3600 | 2360 | 7.41 | 2418 | 8.15 | 2472 | 8.89 | 2525 | 9.65 | 2576 | 10.42 | 2625 | 11.19 | 2673 | 11.92 | 2719 | 12.65 | 2764 | 13.39 | 2807 | 14.14
8816 | 3800 | 2465 | 8.37 | 2521 | 9.13 | 2574 | 9.91 | 2625 | 10.7 | 2675 | 11.51 | 2723 | 12.32 | 2769 | 13.14 | 2814 | 13.9 | 2858 | 14.67 | 2900 | 15.45
9280 | 4000 | 2571 | 9.41 | 2625 | 10.21 | 2676 | 11.03 | 2726 | 11.85 | 2774 | 12.68 | 2821 | 13.53 | 2866 | 14.38 | 2910 | 15.24 | 2953 | 16.05 | 2995 | 16.86
9744 | 4200 | 2678 | 10.55 | 2730 | 11.39 | 2780 | 12.23 | 2828 | 13.09 | 2875 | 13.96 | 2920 | 14.84 | 2964 | 15.72 | 3007 | 16.62 | 3049 | 17.52 | 3090 | 18.37
10208 | 4400 | 2786 | 11.79 | 2836 | 12.66 | 2884 | 13.54 | 2931 | 14.43 | 2976 | 15.33 | 3021 | 16.24 | 3064 | 17.16 | 3106 | 18.09 | 3147 | 19.03 | 3187 | 19.97
10672 | 4600 | 2894 | 13.13 | 2942 | 14.04 | 2989 | 14.95 | 3034 | 15.88 | 3079 | 16.81 | 3122 | 17.75 | 3164 | 18.71 | 3205 | 19.67 | 3245 | 20.64 | 3284 | 21.61
11136 | 4800 | 3003 | 14.56 | 3049 | 15.52 | 3095 | 16.47 | 3139 | 17.43 | 3182 | 18.4 | 3224 | 19.38 | 3265 | 20.36 | 3305 | 21.35 | 3344 | 22.36 | 3382 | 23.37
11600 | 5000 | 3113 | 16.09 | 3157 | 17.12 | 3201 | 18.11 | 3244 | 19.1 | 3286 | 20.1 | 3327 | 21.11 | 3366 | 22.13 | 3406 | 23.16 | 3444 | 24.19 | 3481 | 25.23
12064 | 5200 | 3224 | 17.74 | 3265 | 18.84 | 3308 | 19.86 | 3350 | 20.89 | 3390 | 21.92 | 3430 | 22.97 | 3469 | 24.02 | 3507 | 25.08 | 3544 | 26.14 | 3581 | 27.22
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
5104 | 2200 | 2305 | 7.68 | 2419 | 8.67 | 2526 | 9.66
5568 | 2400 | 2364 | 8.56 | 2477 | 9.61 | 2584 | 10.68 | 2684 | 11.75 | 2781 | 12.85
6032 | 2600 | 2438 | 9.43 | 2537 | 10.62 | 2642 | 11.76 | 2742 | 12.9 | 2838 | 14.06 | 2929 | 15.23 | 3017 | 16.14
6496 | 2800 | 2516 | 10.36 | 2613 | 11.62 | 2705 | 12.89 | 2801 | 14.13 | 2896 | 15.36 | 2987 | 16.59 | 3074 | 17.84 | 3159 | 19.1 | 3240 | 20.37
6960 | 3000 | 2596 | 11.38 | 2691 | 12.69 | 2782 | 14.02 | 2868 | 15.38 | 2955 | 16.73 | 3046 | 18.04 | 3132 | 19.35 | 3216 | 20.68 | 3297 | 22.01 | 3375 | 23.35
7424 | 3200 | 2676 | 12.47 | 2770 | 13.84 | 2860 | 15.24 | 2945 | 16.66 | 3027 | 18.1 | 3106 | 19.56 | 3191 | 20.95 | 3274 | 22.34 | 3355 | 23.74 | 3433 | 25.15
7888 | 3400 | 2758 | 13.65 | 2851 | 15.09 | 2939 | 16.54 | 3023 | 18.02 | 3104 | 19.52 | 3182 | 21.04 | 3257 | 22.58 | 3333 | 24.1 | 3413 | 25.57 | 3491 | 27.04
8352 | 3600 | 2849 | 14.9 | 2933 | 16.42 | 3019 | 17.94 | 3103 | 19.48 | 3183 | 21.04 | 3259 | 22.61 | 3334 | 24.21 | 3405 | 25.83 | 3475 | 27.46 | 3550 | 29.04
8816 | 3800 | 2942 | 16.24 | 3022 | 17.83 | 3101 | 19.44 | 3183 | 21.03 | 3262 | 22.65 | 3338 | 24.29 | 3411 | 25.94 | 3482 | 27.62 | 3551 | 29.31 | 3618 | 31.02
9280 | 4000 | 3035 | 17.67 | 3114 | 19.33 | 3189 | 21 | 3265 | 22.69 | 3342 | 24.37 | 3417 | 26.07 | 3490 | 27.78 | 3560 | 29.52 | 3628 | 31.27 | 3694 | 33.03
9744 | 4200 | 3130 | 19.22 | 3207 | 20.93 | 3281 | 22.67 | 3352 | 24.43 | 3424 | 26.2 | 3498 | 27.96 | 3569 | 29.73 | 3639 | 31.52 | 3706 | 33.33 | 3772 | 35.15
10208 | 4400 | 3226 | 20.87 | 3301 | 22.65 | 3374 | 24.44 | 3444 | 26.26 | 3512 | 28.11 | 3579 | 29.96 | 3650 | 31.79 | 3719 | 33.64 | 3785 | 35.51 | 3850 | 37.39
10672 | 4600 | 3322 | 22.6 | 3396 | 24.48 | 3468 | 26.33 | 3536 | 28.21 | 3603 | 30.12 | 3667 | 32.04 | 3732 | 33.97 | 3799 | 35.88 | 3865 | 37.81 | 3929 | 39.75
11136 | 4800 | 3420 | 24.38 | 3493 | 26.43 | 3562 | 28.35 | 3630 | 30.28 | 3695 | 32.25 | 3759 | 34.23 | 3820 | 36.23 | 3881 | 38.25 | 3946 | 40.23