## Sheet1
AIRFOIL BLADE
SIZE S - AF - 73 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 73 inches 1854 mm | [13 empty] | SIZE 73 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel Circumference 19.1 feet 5.822 m | [13 empty] | CLASS I |  | 564
Inlet Diameter / Area 82 ⅜ inches Dia/36.3 sq f.t 2092 mm /3.372 m² | [13 empty] | CLASS II |  | 736
Outlet Size Area 76 15/16*57 11/16 Inches I.D/30.82 sq.ft 1954*1465 mm/2.863m² | [13 empty] | CLASS III |  | 927
Tip Speed 19.1* rpm ft./minute 5.822*RPM m/minute | [13 empty] | CLASS IV |  | 1020
Maximum BHP 417.40*(RPM÷1000)³ BHP 311.3 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
18492 | 600 | 133 | 0.96 | 149 | 1.36 | 168 | 1.81
21574 | 700 | 143 | 1.18 | 159 | 1.66 | 173 | 2.13 | 189 | 2.64 | 204 | 3.17
24656 | 800 | 154 | 1.44 | 169 | 1.98 | 183 | 2.52 | 195 | 3.05 | 208 | 3.62 | 222 | 4.22 | 235 | 4.84
27738 | 900 | 166 | 1.75 | 180 | 2.33 | 193 | 2.95 | 205 | 3.55 | 216 | 4.14 | 227 | 4.76 | 239 | 5.42 | 263 | 6.8
30820 | 1000 | 178 | 2.12 | 190 | 2.73 | 203 | 3.39 | 215 | 4.08 | 226 | 4.75 | 236 | 5.41 | 246 | 6.09 | 267 | 7.53 | 288 | 9.06
33902 | 1100 | 191 | 2.55 | 203 | 3.21 | 214 | 3.9 | 225 | 4.64 | 236 | 5.4 | 246 | 6.14 | 256 | 6.86 | 273 | 8.34 | 293 | 9.94 | 312 | 11.61
36984 | 1200 | 204 | 3.04 | 215 | 3.75 | 225 | 4.48 | 236 | 5.26 | 246 | 6.06 | 256 | 6.89 | 265 | 7.71 | 283 | 9.28 | 299 | 10.91 | 317 | 12.65
40066 | 1300 | 217 | 3.61 | 228 | 4.36 | 238 | 5.14 | 247 | 5.94 | 257 | 6.8 | 266 | 7.67 | 275 | 8.56 | 292 | 10.31 | 308 | 12.03 | 323 | 13.79
43148 | 1400 | 231 | 4.26 | 241 | 5.06 | 250 | 5.88 | 259 | 6.73 | 268 | 7.61 | 277 | 8.52 | 286 | 9.46 | 302 | 11.39 | 318 | 13.25 | 333 | 15.1
46230 | 1500 | 244 | 4.95 | 254 | 5.83 | 263 | 6.71 | 271 | 7.6 | 279 | 8.51 | 288 | 9.46 | 296 | 10.45 | 313 | 12.47 | 328 | 14.56 | 342 | 16.51
49312 | 1600 | 258 | 5.73 | 267 | 6.7 | 276 | 7.62 | 284 | 8.56 | 292 | 9.52 | 299 | 10.5 | 307 | 11.52 | 323 | 13.64 | 338 | 15.82 | 352 | 18.03
52394 | 1700 | 272 | 6.6 | 281 | 7.67 | 289 | 8.64 | 297 | 9.62 | 304 | 10.63 | 312 | 11.65 | 319 | 12.7 | 334 | 14.89 | 348 | 17.17 | 362 | 19.5
55476 | 1800 | 286 | 7.57 | 294 | 8.69 | 302 | 9.75 | 310 | 10.79 | 317 | 11.84 | 324 | 12.91 | 331 | 14 | 345 | 16.25 | 359 | 18.62 | 373 | 21.04
58558 | 1900 | 300 | 8.63 | 308 | 9..81 | 316 | 10.97 | 323 | 12.06 | 330 | 13.16 | 337 | 14.28 | 344 | 15.41 | 356 | 17.73 | 370 | 20.17 | 383 | 22.69
61640 | 2000 | 314 | 9.81 | 322 | 11.04 | 329 | 12.3 | 336 | 13.44 | 343 | 14.59 | 350 | 15.76 | 356 | 16.94 | 368 | 19.35 | 381 | 21.84 | 394 | 24.45
67804 | 2200 | 342 | 12.49 | 349 | 13.83 | 356 | 15.2 | 363 | 16.58 | 370 | 17.83 | 376 | 19.09 | 382 | 20.36 | 394 | 22.96 | 405 | 25.61 | 415 | 28.32
73968 | 2400 | 371 | 15.66 | 377 | 17.12 | 384 | 18.59 | 390 | 20.09 | 396 | 21.59 | 402 | 22.95 | 408 | 24.32 | 419 | 27.1 | 430 | 29.94 | 440 | 32.83
80132 | 2600 | 399 | 19.37 | 406 | 20.93 | 412 | 22.52 | 418 | 24.13 | 423 | 25.76 | 429 | 27.39 | 435 | 28.85 | 445 | 31.82 | 455 | 34.85 | 465 | 37.92
86296 | 2800 | 428 | 23.65 | 434 | 25.33 | 440 | 27.03 | 445 | 28.75 | 451 | 30.48 | 456 | 32.24 | 461 | 34.01 | 472 | 37.17 | 481 | 40.39 | 491 | 43.64
92460 | 3000 | 457 | 28.56 | 462 | 30.35 | 468 | 32.16 | 473 | 33.99 | 487 | 35.83 | 484 | 37.69 | 489 | 39.57 | 498 | 43.2 | 508 | 46.6 | 517 | 50.05
98624 | 3200 | 486 | 34.14 | 491 | 36.04 | 496 | 37.96 | 501 | 39.9 | 506 | 41.85 | 511 | 43.82 | 516 | 45.81 | 525 | 49.83 | 534 | 53.54 | 543 | 57.17
104788 | 3400 | 515 | 40.43 | 520 | 42.44 | 525 | 44.48 | 530 | 46.52 | 534 | 48.59 | 539 | 50.67 | 543 | 52.76 | 552 | 56.99 | 561 | 61.24 | 569 | 65.07
110952 | 3600 | 544 | 47.47 | 549 | 49.6 | 553 | 51.74 | 558 | 53.9 | 562 | 56.08 | 567 | 58.26 | 571 | 60.47 | 580 | 64.92 | 588 | 69.42 | 596 | 73.78
117116 | 3800 | 573 | 55.32 | 578 | 57.56 | 582 | 59.81 | 586 | 62.08 | 591 | 64.37 | 595 | 66.67 | 599 | 68.98 | 607 | 73.64 | 615 | 78.36 | 623 | 83.13
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
43148 | 1400 | 346 | 16.99 | 377 | 21.07 | 407 | 25.35
46230 | 1500 | 356 | 18.49 | 381 | 22.59 | 411 | 27.09 | 439 | 31.69
49312 | 1600 | 365 | 20.11 | 390 | 24.37 | 416 | 28.89 | 443 | 33.71 | 469 | 38.63
52394 | 1700 | 375 | 21.84 | 400 | 26.28 | 422 | 30.86 | 448 | 35.79 | 473 | 40.92 | 497 | 46.15
55476 | 1800 | 385 | 23.53 | 410 | 28.32 | 432 | 33.08 | 453 | 37.98 | 478 | 43.28 | 502 | 48.72 | 524 | 54.25
58558 | 1900 | 396 | 25.27 | 419 | 30.49 | 441 | 35.43 | 462 | 40.51 | 482 | 45.72 | 506 | 51.38 | 529 | 57.12 | 550 | 62.94
61640 | 2000 | 406 | 27.12 | 429 | 32.61 | 451 | 37.92 | 472 | 43.18 | 491 | 48.55 | 510 | 54.11 | 533 | 60.07 | 555 | 66.1 | 575 | 72.22 | 595 | 78.41
67804 | 2200 | 427 | 31.17 | 450 | 37.02 | 471 | 43.07 | 491 | 48.96 | 510 | 54.69 | 528 | 60.53 | 545 | 66.48 | 564 | 72.68 | 584 | 79.22 | 604 | 85.83
73968 | 2400 | 450 | 35.77 | 471 | 41.96 | 492 | 48.36 | 511 | 54.94 | 530 | 64.49 | 547 | 67.69 | 564 | 73.99 | 580 | 80.38 | 596 | 86.87 | 613 | 93.63
80132 | 2600 | 475 | 41.04 | 493 | 47.45 | 513 | 54.23 | 532 | 61.16 | 550 | 68.26 | 567 | 75.52 | 584 | 82.2 | 600 | 88.96 | 615 | 95.8 | 630 | 102.73
86296 | 2800 | 500 | 46.95 | 517 | 53.69 | 535 | 60.69 | 553 | 68 | 571 | 75.45 | 587 | 83.06 | 603 | 90.82 | 619 | 98.28 | 634 | 105.49 | 649 | 112.78
92460 | 3000 | 525 | 53.54 | 542 | 60.64 | 558 | 67.92 | 575 | 75.48 | 592 | 83.3 | 608 | 91.27 | 624 | 99.38 | 639 | 107.62 | 654 | 115.99 | 668 | 123.64
98624 | 3200 | 551 | 60.85 | 567 | 68.32 | 583 | 75.96 | 597 | 83.74 | 613 | 91.84 | 629 | 100.18 | 645 | 108.64 | 660 | 117.24 | 674 | 125.96 | 688 | 134.81
104788 | 3400 | 577 | 68.93 | 593 | 76.78 | 608 | 84.78 | 622 | 92.92 | 636 | 101.21 | 651 | 109.82 | 666 | 118.65 | 681 | 127.61 | 695 | 136.69 | 709 | 145.89
110952 | 3600 | 604 | 77.83 | 619 | 86.05 | 633 | 94.42 | 647 | 102.93 | 660 | 111.57 | 673 | 120.34 | 687 | 129.45 | 702 | 138.77 | 716 | 148.21 | 729 | 157.76
117116 | 3800 | 631 | 87.6 | 645 | 96.19 | 659 | 104.93 | 672 | 113.8 | 685 | 122.81 | 698 | 131.94 | 710 | 141.19 | 723 | 150.76 | 737 | 160.56 | 750 | 170.48
123280 | 4000 | 657 | 98.16 | 671 | 107.25 | 685 | 116.36 | 698 | 125.6 | 711 | 134.96 | 723 | 144.45 | 735 | 154.06 | 746 | 163.78 | 759 | 173.79 | 772 | 184.07
129444 | 4200 | 684 | 109.26 | 698 | 119.26 | 711 | 128.74 | 724 | 138.35 | 736 | 148.08 | 748 | 157.93 | 760 | 167.89 | 771 | 177.97 | 782 | 188.16 | 793 | 198.58
135608 | 4400 | 712 | 121.3 | 725 | 132.28 | 738 | 142.14 | 750 | 152.12 | 762 | 162.21 | 774 | 172.43 | 785 | 182.75 | 796 | 193.18 | 807 | 203.72 | 817 | 214.36
141772 | 4600 | 739 | 134.32 | 752 | 145.79 | 764 | 156.59 | 776 | 166.94 | 788 | 177.4 | 799 | 187.98 | 810 | 198.66 | 821 | 209.45 | 831 | 220.34 | 842 | 231.34
147936 | 4800 | 767 | 148.37 | 779 | 160.25 | 791 | 172.13 | 803 | 182.86 | 814 | 193.7 | 825 | 204.64 | 836 | 215.68 | 846 | 226.83 | 857 | 238.08 | 867 | 249.43
154100 | 5000 | 794 | 163.48 | 806 | 175.79 | 818 | 188.28 | 829 | 199.93 | 840 | 211.14 | 851 | 222.45 | 862 | 233.85 | 872 | 245.36 | 882 | 256.97 | 892 | 268.67
160264 | 5200 | 822 | 179.7 | 834 | 192.43 | 845 | 205.32 | 856 | 218.2 | 867 | 229.77 | 877 | 241.45 | 888 | 253.22 | 898 | 265.09 | 907 | 277.06 | 917 | 289.11
166428 | 5400 | 850 | 197.07 | 861 | 210.23 | 872 | 223.54 | 883 | 236.98 | 894 | 249.65 | 904 | 261.7 | 914 | 273.84 | 924 | 286.07 | 933 | 298.39 | 942 | 310.81
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
73968 | 2400 | 632 | 100.74 | 668 | 115.16 | 702 | 129.83
80132 | 2600 | 644 | 109.75 | 676 | 124.63 | 710 | 140.14 | 742 | 155.9 | 773 | 171.88
86296 | 2800 | 663 | 120.16 | 690 | 135.14 | 719 | 150.89 | 751 | 167.49 | 781 | 184.3 | 810 | 201.33
92460 | 3000 | 682 | 131.38 | 709 | 147.07 | 734 | 163.06 | 760 | 179.54 | 790 | 197.2 | 819 | 215.06 | 847 | 233.13 | 873 | 251.39
98624 | 3200 | 702 | 143.46 | 728 | 159.87 | 753 | 176.57 | 777 | 193.55 | 800 | 210.79 | 828 | 229.29 | 855 | 248.19 | 882 | 267.28 | 907 | 286.55 | 932 | 305.99
104788 | 3400 | 722 | 155.2 | 748 | 173.6 | 772 | 191.01 | 796 | 208.69 | 819 | 226.63 | 840 | 244.82 | 864 | 263.78 | 891 | 283.71 | 916 | 303.81 | 941 | 324.07
110952 | 3600 | 742 | 167.43 | 768 | 187.1 | 792 | 206.43 | 815 | 224.82 | 838 | 243.46 | 859 | 262.35 | 880 | 281.47 | 900 | 300.83 | 925 | 321.62 | 950 | 342.72
117116 | 3800 | 763 | 180.5 | 788 | 200.87 | 812 | 221.65 | 835 | 241.98 | 857 | 261.34 | 878 | 280.92 | 899 | 300.74 | 919 | 320.77 | 938 | 341.03 | 958 | 361.95
123280 | 4000 | 784 | 194.45 | 809 | 215.53 | 832 | 237.01 | 855 | 258.88 | 876 | 280.29 | 897 | 300.59 | 918 | 321.1 | 937 | 341.83 | 956 | 362.77 | 975 | 383.92
129444 | 4200 | 806 | 209.32 | 830 | 231.12 | 853 | 253.3 | 875 | 275.87 | 896 | 298.8 | 917 | 321.4 | 937 | 342.62 | 956 | 364.05 | 975 | 385.68 | 994 | 407.51
135608 | 4400 | 828 | 225.16 | 851 | 247.67 | 874 | 270.57 | 896 | 293.83 | 917 | 317.45 | 937 | 341.43 | 956 | 365.32 | 976 | 387.46 | 994 | 409.78 | 1013 | 432.3
141772 | 4600 | 852 | 242.43 | 873 | 265.24 | 895 | 288.85 | 917 | 312.82 | 937 | 337.13 | 957 | 361.79 | 977 | 386.78 | 995 | 412.09 | 1014 | 435.14
147936 | 4800 | 876 | 260.87 | 895 | 284.05 | 917 | 308.18 | 938 | 332.86 | 958 | 357.88 | 978 | 383.23 | 997 | 408.9 | 1015 | 434.88
154100 | 5000 | 901 | 280.46 | 920 | 304.33 | 938 | 328.61 | 959 | 354.01 | 979 | 379.73 | 999 | 405.77 | 1017 | 432.13