## Sheet1
AIRFOIL BLADE
SIZE S - AF - 81 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 80 ¾ inches 2051 mm | [13 empty] | SIZE 81 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel Circumference 21.1 feet 6.431 m | [13 empty] | CLASS I |  | 510
Inlet Diameter / Area 90 ⅛ inches Dia/43.6 sq f.t 2289 mm /4.050 m² | [13 empty] | CLASS II |  | 665
Outlet Size Area 85 ⅛*63 ⅝ Inches I.D/37.61 sq.ft 2162*1616 mm/3.494m² | [13 empty] | CLASS III |  | 838
Tip Speed 21.1* rpm ft./minute 6.431*RPM m/minute | [13 empty] | CLASS IV |  | 922
Maximum BHP 690.82*(RPM÷1000)³ BHP 515.1 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
22566 | 600 | 120 | 1.18 | 135 | 1.66 | 151 | 2.21
26327 | 700 | 129 | 1.44 | 144 | 2.02 | 156 | 2.59 | 170 | 3.22 | 184 | 3.87
30088 | 800 | 139 | 1.76 | 153 | 2.41 | 165 | 3.07 | 176 | 3.72 | 188 | 4.41 | 200 | 5.15 | 212 | 5.91
33849 | 900 | 149 | 2.13 | 162 | 2.84 | 174 | 3.59 | 185 | 4.32 | 195 | 5.05 | 205 | 5.8 | 216 | 6.62 | 237 | 8.3
37610 | 1000 | 161 | 2.58 | 172 | 3.33 | 183 | 4.14 | 194 | 4.98 | 204 | 5.79 | 213 | 6.6 | 222 | 7.42 | 241 | 9.19 | 261 | 11.06
41371 | 1100 | 172 | 3.1 | 183 | 3.9 | 193 | 4.76 | 203 | 5.65 | 213 | 6.58 | 222 | 7.48 | 231 | 8.36 | 247 | 10.17 | 265 | 12.13 | 282 | 14.15
45132 | 1200 | 184 | 3.7 | 194 | 4.56 | 203 | 5.46 | 213 | 6.41 | 222 | 7.39 | 231 | 8.4 | 240 | 9.4 | 255 | 11.32 | 270 | 13.3 | 286 | 15.44
48893 | 1300 | 196 | 4.39 | 206 | 5.31 | 214 | 6.26 | 223 | 7.24 | 232 | 8.28 | 241 | 9.35 | 249 | 10.44 | 264 | 12.58 | 278 | 14.67 | 292 | 16.82
52654 | 1400 | 208 | 5.18 | 217 | 6.15 | 226 | 7.16 | 234 | 8.19 | 242 | 9.27 | 250 | 10.39 | 258 | 11.53 | 273 | 13.89 | 287 | 16.15 | 300 | 18.41
56415 | 1500 | 220 | 6.02 | 229 | 7.1 | 237 | 8.16 | 245 | 9.25 | 252 | 10.37 | 260 | 11.53 | 268 | 12.73 | 282 | 15.2 | 296 | 17.76 | 309 | 20.13
60176 | 1600 | 233 | 6.97 | 241 | 8.15 | 249 | 9.28 | 256 | 10.42 | 263 | 11.6 | 270 | 12.79 | 277 | 14.04 | 292 | 16.62 | 305 | 19.29 | 318 | 21.98
63937 | 1700 | 245 | 8.03 | 253 | 9.33 | 261 | 10.51 | 268 | 11.71 | 275 | 12.94 | 281 | 14.19 | 288 | 15.47 | 301 | 18.15 | 315 | 20.93 | 327 | 23.78
67698 | 1800 | 258 | 9.2 | 265 | 10.57 | 273 | 11.86 | 280 | 13.13 | 286 | 14.41 | 293 | 15.72 | 299 | 17.05 | 311 | 19.8 | 324 | 22.69 | 336 | 25.66
71459 | 1900 | 270 | 10.49 | 278 | 11.93 | 285 | 13.35 | 291 | 14.67 | 298 | 16.01 | 304 | 17.38 | 310 | 18.76 | 321 | 21.6 | 334 | 24.58 | 346 | 27.66
75220 | 2000 | 283 | 11.92 | 290 | 13.42 | 297 | 14.96 | 303 | 16.35 | 310 | 17.76 | 316 | 19.18 | 321 | 20.62 | 332 | 23.56 | 344 | 26.61 | 355 | 29.8
82742 | 2200 | 308 | 15.18 | 315 | 16.82 | 321 | 18.48 | 328 | 20.17 | 333 | 21.69 | 339 | 23.23 | 345 | 24.78 | 355 | 27.95 | 365 | 31.19 | 375 | 34.5
90264 | 2400 | 334 | 19.03 | 340 | 20.8 | 346 | 22.61 | 352 | 24.44 | 358 | 26.26 | 363 | 27.92 | 368 | 29.59 | 378 | 32.99 | 388 | 36.45 | 397 | 39.98
97786 | 2600 | 360 | 23.53 | 366 | 25.44 | 371 | 27.38 | 377 | 29.34 | 382 | 31.33 | 387 | 33.31 | 392 | 35.1 | 402 | 38.73 | 411 | 42.42 | 420 | 46.17
105308 | 2800 | 386 | 28.73 | 391 | 30.78 | 397 | 32.85 | 402 | 34.95 | 407 | 37.07 | 411 | 39.21 | 416 | 41.36 | 425 | 45.23 | 434 | 49.15 | 443 | 53.13
112830 | 3000 | 412 | 34.69 | 417 | 36.44 | 422 | 39.09 | 427 | 41.31 | 431 | 43.57 | 436 | 45.84 | 441 | 48.13 | 449 | 52.54 | 458 | 56.7 | 466 | 60.9
120352 | 3200 | 438 | 41.46 | 443 | 43.79 | 448 | 46.13 | 452 | 48.49 | 457 | 50.88 | 461 | 53.28 | 465 | 55.71 | 474 | 60.61 | 482 | 65.7 | 490 | 69.56
127874 | 3400 | 464 | 49.1 | 469 | 51.56 | 473 | 54.04 | 478 | 56.54 | 482 | 59.05 | 486 | 61.59 | 490 | 64.15 | 498 | 69.32 | 506 | 74.48 | 514 | 79.15
135396 | 3600 | 491 | 57.65 | 495 | 60.25 | 499 | 62.86 | 503 | 65.5 | 507 | 68.15 | 511 | 70.82 | 515 | 73.51 | 523 | 78.94 | 530 | 84.44 | 538 | 89.73
142918 | 3800 | 517 | 67.17 | 521 | 69.91 | 525 | 72.66 | 529 | 75.43 | 533 | 78.22 | 537 | 81.02 | 540 | 83.84 | 548 | 89.54 | 555 | 95.3 | 562 | 101.12
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
52654 | 1400 | 313 | 20.72 | 341 | 25.71 | 368 | 30.94
56415 | 1500 | 321 | 22.55 | 345 | 27.56 | 372 | 33.06 | 397 | 38.68
60176 | 1600 | 330 | 24.51 | 352 | 29.72 | 376 | 35.25 | 400 | 41.13 | 424 | 47.14
63937 | 1700 | 339 | 26.62 | 361 | 32.05 | 382 | 37.65 | 404 | 43.67 | 428 | 49.94 | 449 | 56.32
67698 | 1800 | 348 | 28.69 | 370 | 34.53 | 390 | 40.34 | 409 | 46.32 | 432 | 52.82 | 453 | 59.46 | 474 | 66.22
71459 | 1900 | 357 | 30.8 | 379 | 37.16 | 399 | 43.21 | 417 | 49.4 | 436 | 55.79 | 457 | 62.7 | 478 | 69.71 | 497 | 76.82
75220 | 2000 | 367 | 33.05 | 388 | 39.76 | 407 | 46.23 | 426 | 52.65 | 443 | 59.21 | 461 | 66.03 | 482 | 73.3 | 501 | 80.67 | 520 | 88.14 | 538 | 95.7
82742 | 2200 | 386 | 37.99 | 406 | 45.13 | 425 | 52.52 | 443 | 59.69 | 461 | 66.69 | 477 | 73.82 | 492 | 81.08 | 509 | 88.69 | 528 | 96.67 | 546 | 104.75
90264 | 2400 | 406 | 43.57 | 425 | 51.14 | 444 | 58.96 | 462 | 67 | 478 | 74.95 | 494 | 82.53 | 509 | 90.22 | 524 | 98.03 | 538 | 105.96 | 554 | 114.25
97786 | 2600 | 428 | 49.98 | 445 | 57.82 | 463 | 66.09 | 480 | 74.56 | 496 | 83.23 | 512 | 92.07 | 527 | 100.21 | 541 | 108.47 | 555 | 116.83 | 569 | 125.29
105308 | 2800 | 451 | 57.16 | 467 | 65.4 | 482 | 73.95 | 499 | 82.87 | 515 | 91.98 | 530 | 101.27 | 545 | 110.74 | 559 | 119.81 | 573 | 128.62 | 586 | 137.52
112830 | 3000 | 474 | 65.17 | 489 | 73.85 | 503 | 82.73 | 519 | 91.97 | 534 | 101.52 | 549 | 111.26 | 563 | 121.16 | 577 | 131.22 | 590 | 141.39 | 603 | 150.73
120352 | 3200 | 497 | 74.05 | 512 | 83.18 | 526 | 92.5 | 539 | 102.01 | 553 | 111.91 | 568 | 122.09 | 582 | 132.43 | 596 | 142.93 | 609 | 153.58 | 621 | 164.39
127874 | 3400 | 521 | 83.87 | 535 | 93.45 | 548 | 103.22 | 561 | 113.17 | 574 | 123.28 | 587 | 133.82 | 601 | 144.6 | 614 | 155.54 | 627 | 166.636 | 640 | 177.86
135396 | 3600 | 545 | 94.68 | 558 | 104.72 | 571 | 114.94 | 584 | 125.33 | 596 | 135.88 | 608 | 146.6 | 621 | 157.74 | 634 | 169.12 | 646 | 180.64 | 658 | 192.31
142918 | 3800 | 569 | 106.55 | 582 | 117.04 | 595 | 127.71 | 607 | 138.54 | 618 | 149.54 | 630 | 160.69 | 641 | 171.99 | 653 | 183.7 | 665 | 195.67 | 677 | 207.77
150440 | 4000 | 593 | 119.41 | 606 | 130.47 | 618 | 141.59 | 630 | 152.87 | 641 | 164.31 | 652 | 175.9 | 663 | 187.63 | 673 | 199.5 | 685 | 211.75 | 697 | 224.3
157962 | 4200 | 617 | 132.9 | 630 | 145.06 | 642 | 156.64 | 653 | 168.38 | 664 | 180.26 | 675 | 192.28 | 685 | 204.45 | 696 | 216.75 | 706 | 229.2 | 716 | 241.95
165484 | 4400 | 642 | 147.52 | 654 | 160.88 | 665 | 172.92 | 677 | 185.1 | 687 | 197.43 | 698 | 209.9 | 708 | 222.5 | 718 | 235.24 | 728 | 248.11 | 737 | 261.11
173006 | 4600 | 667 | 163.34 | 678 | 177.34 | 689 | 190.47 | 700 | 203.11 | 711 | 215.88 | 721 | 228.8 | 731 | 241.84 | 741 | 255.01 | 750 | 268.32 | 759 | 281.74
180528 | 4800 | 691 | 180.39 | 703 | 194.91 | 714 | 209.36 | 724 | 222.45 | 734 | 235.68 | 744 | 249.04 | 754 | 262.52 | 764 | 276.14 | 773 | 289.87 | 782 | 303.73
188050 | 5000 | 716 | 198.75 | 727 | 213.77 | 738 | 228.99 | 748 | 243.19 | 758 | 256.87 | 768 | 270.67 | 777 | 284.6 | 787 | 298.66 | 796 | 312.83 | 805 | 327.12
195572 | 5200 | 741 | 218.44 | 752 | 233.99 | 762 | 249.72 | 772 | 265.37 | 782 | 279.51 | 791 | 293.77 | 801 | 308.14 | 810 | 322.63 | 819 | 337.24 | 827 | 351.96
203094 | 5400 | 767 | 239.55 | 777 | 255.61 | 787 | 271.85 | 797 | 288.27 | 806 | 303.66 | 815 | 318.36 | 824 | 333.19 | 833 | 348.12 | 842 | 363.17 | 850 | 378.33
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
90264 | 2400 | 571 | 122.93 | 603 | 140.54 | 634 | 158.47
97786 | 2600 | 582 | 133.87 | 611 | 152.08 | 642 | 171.03 | 671 | 190.27 | 698 | 209.79
105308 | 2800 | 599 | 146.53 | 623 | 164.83 | 650 | 184.12 | 679 | 204.39 | 706 | 224.93 | 732 | 245.73
112830 | 3000 | 616 | 160.18 | 640 | 179.34 | 663 | 198.88 | 686 | 219.07 | 714 | 240.64 | 740 | 262.46 | 765 | 284.52 | 789 | 306.82
120352 | 3200 | 634 | 174.88 | 658 | 194.92 | 680 | 215.32 | 702 | 236.05 | 722 | 257.12 | 748 | 279.8 | 773 | 302.88 | 797 | 326.19 | 820 | 349.73 | 842 | 373.48
127874 | 3400 | 652 | 189.24 | 675 | 211.62 | 697 | 232.89 | 719 | 254.48 | 739 | 276.39 | 759 | 298.61 | 781 | 321.88 | 805 | 346.21 | 828 | 370.76 | 850 | 395.51
135396 | 3600 | 670 | 204.12 | 693 | 228.14 | 715 | 251.64 | 736 | 274.11 | 756 | 296.88 | 776 | 319.94 | 795 | 343.3 | 813 | 366.94 | 836 | 392.46 | 858 | 418.24
142918 | 3800 | 689 | 220.02 | 712 | 244.89 | 733 | 270.28 | 754 | 294.99 | 774 | 318.62 | 793 | 342.54 | 812 | 366.74 | 830 | 391.22 | 847 | 415.97 | 866 | 441.66
150440 | 4000 | 708 | 236.98 | 730 | 262.73 | 751 | 288.97 | 772 | 315.68 | 791 | 341.69 | 810 | 366.47 | 829 | 391.53 | 847 | 416.85 | 864 | 442.42 | 881 | 468.26
157962 | 4200 | 727 | 255.07 | 749 | 281.69 | 770 | 308.78 | 790 | 336.34 | 809 | 364.36 | 828 | 391.78 | 846 | 417.7 | 864 | 443.87 | 881 | 470.29 | 897 | 496.96
165484 | 4400 | 747 | 274.33 | 768 | 301.82 | 789 | 329.78 | 809 | 358.2 | 828 | 387.05 | 846 | 416.33 | 864 | 445.32 | 881 | 472.36 | 898 | 499.63 | 914 | 527.13
173006 | 4600 | 769 | 295.29 | 788 | 323.18 | 808 | 352.02 | 827 | 381.29 | 846 | 410.99 | 864 | 441.11 | 882 | 471.62 | 899 | 502.35 | 915 | 530.48
180528 | 4800 | 791 | 317.7 | 808 | 346.01 | 827 | 375.53 | 846 | 405.67 | 865 | 436.22 | 883 | 467.18 | 900 | 498.54 | 917 | 530.28
188050 | 5000 | 813 | 341.52 | 830 | 370.67 | 847 | 400.37 | 866 | 431.38 | 884 | 462.8 | 902 | 494.6 | 919 | 526.8