## Sheet1
AIRFOIL BLADE
SIZE S - AF - 33 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 33inches 838 mm | [13 empty] | SIZE 33 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 8.64 feet 2.633 m | [13 empty] | CLASS I |  | 1265
Inlet Diameter / Area 35 11/16 inches Dia/6.87 sq f.t 906mm /.6382 m² | [13 empty] | CLASS II |  | 1652
Outlet Size Area 34 11/16*26 Inches I.D/6.26 sq.ft 881*660mm/.5816m² | [13 empty] | CLASS III |  | 2083
Tip Speed 8.64 * rpm ft./minute 2.633*RPM m/minute | [13 empty] | CLASS IV |  | 2291
Maximum BHP 8.25*(RPM÷1000)³ BHP 6.152* (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
3756 | 600 | 291 | 0.2 | 328 | 0.29 | 365 | 0.38 | 404 | 0.48
4382 | 700 | 315 | 0.25 | 349 | 0.35 | 380 | 0.45 | 410 | 0.55 | 445 | 0.67
5008 | 800 | 341 | 0.31 | 372 | 0.42 | 401 | 0.53 | 428 | 0.64 | 455 | 0.75 | 483 | 0.88 | 513 | 1.02
5634 | 900 | 368 | 0.39 | 397 | 0.5 | 423 | 0.62 | 449 | 0.75 | 474 | 0.87 | 498 | 1 | 521 | 1.13 | 574 | 1.43
6260 | 1000 | 397 | 0.47 | 424 | 0.6 | 448 | 0.73 | 472 | 0.87 | 495 | 1 | 517 | 1.14 | 539 | 1.28 | 581 | 1.56 | 630 | 1.9 | 675 | 2.26
6886 | 1100 | 426 | 0.57 | 451 | 0.71 | 475 | 0.85 | 497 | 1 | 518 | 1.14 | 539 | 1.29 | 560 | 1.44 | 299 | 1.75 | 637 | 2.07 | 681 | 2.44
7512 | 1200 | 456 | 0.68 | 479 | 0.83 | 501 | 0.98 | 523 | 1.14 | 543 | 1.3 | 562 | 1.46 | 582 | 1.62 | 619 | 1.95 | 655 | 2.29 | 690 | 2.63
8138 | 1300 | 486 | 0.81 | 508 | 0.97 | 529 | 1.13 | 549 | 1.3 | 569 | 1.47 | 587 | 1.65 | 60 | 1.82 | 641 | 2.17 | 675 | 2.53 | 708 | 2.9
8764 | 1400 | 516 | 0.96 | 537 | 1.13 | 557 | 1.3 | 576 | 1.48 | 595 | 1.66 | 613 | 1.85 | 630 | 2.03 | 663 | 2.41 | 697 | 2.79 | 728 | 3.18
9390 | 1500 | 547 | 1.12 | 567 | 1.31 | 586 | 1.49 | 604 | 1.68 | 622 | 1.87 | 639 | 2.07 | 656 | 2.27 | 688 | 2.67 | 719 | 3.07 | 750 | 3.48
10016 | 1600 | 577 | 1.3 | 597 | 1.51 | 616 | 1.7 | 633 | 1.9 | 650 | 2.1 | 666 | 2.3 | 683 | 2.51 | 714 | 2.94 | 743 | 3.37 | 772 | 3.8
10642 | 1700 | 609 | 1.5 | 627 | 1.72 | 645 | 1.94 | 662 | 2.14 | 678 | 2.35 | 694 | 2.57 | 709 | 2.79 | 740 | 3.23 | 768 | 3.69 | 795 | 4.14
11268 | 1800 | 640 | 1.72 | 658 | 1.96 | 675 | 2.19 | 691 | 2.41 | 707 | 2.63 | 722 | 2.85 | 737 | 3.08 | 766 | 3.55 | 794 | 4.03 | 820 | 4.51
11894 | 1900 | 671 | 1.97 | 689 | 2.21 | 705 | 2.47 | 721 | 2.7 | 736 | 2.93 | 751 | 3.17 | 765 | 3.4 | 793 | 3.89 | 820 | 4.39 | 846 | 4.9
12520 | 2000 | 703 | 2.24 | 720 | 2.5 | 736 | 2.76 | 751 | 3.02 | 766 | 3.26 | 780 | 3.51 | 794 | 3.75 | 820 | 4.26 | 846 | 4.78 | 872 | 5.31
13772 | 2200 | 767 | 2.86 | 782 | 3.14 | 797 | 3.43 | 812 | 3.72 | 825 | 4.01 | 839 | 4.27 | 852 | 4.54 | 877 | 5.08 | 901 | 5.64 | 925 | 6.2
15024 | 2400 | 831 | 3.6 | 845 | 3.9 | 859 | 4.21 | 873 | 4.53 | 886 | 4.85 | 899 | 5.16 | 911 | 5.45 | 935 | 6.03 | 957 | 6.63 | 979 | 7.23
16276 | 2600 | 895 | 4.46 | 909 | 4.79 | 922 | 5.12 | 935 | 5.46 | 947 | 5.8 | 959 | 6.15 | 971 | 6.5 | 993 | 7.12 | 1015 | 7.75 | 1036 | 8.39
17528 | 2800 | 960 | 5.45 | 973 | 5.81 | 985 | 6.17 | 997 | 6.53 | 1009 | 6.89 | 1020 | 7.26 | 1031 | 7.64 | 1053 | 8.35 | 1074 | 9.02 | 1094 | 9.71
18780 | 3000 | 1025 | 6.59 | 1037 | 6.97 | 1048 | 7.36 | 1060 | 7.74 | 1071 | 8.13 | 1082 | 8.52 | 1093 | 8.92 | 1113 | 9.72 | 1133 | 10.46 | 1152 | 11.18
20032 | 3200 | 1090 | 7.89 | 1101 | 8.29 | 1112 | 8.7 | 1123 | 9.11 | 1134 | 9.52 | 1144 | 9.94 | 1154 | 10.36 | 1174 | 11.2 | 1193 | 12.06 | 1212 | 12.82
21284 | 3400 | 1156 | 9.36 | 1166 | 9.78 | 1177 | 10.21 | 1187 | 10.64 | 1197 | 11.08 | 1207 | 11.52 | 1216 | 11.96 | 1235 | 12.85 | 1254 | 13.76 | 1272 | 14.64
22536 | 3600 | 1221 | 11 | 1231 | 11.45 | 1241 | 11.9 | 1251 | 12.36 | 1260 | 12.82 | 1270 | 13.28 | 1279 | 13.74 | 1297 | 14.68 | 1315 | 15.63 | 1332 | 16.59
23788 | 3800 | 1287 | 12.82 | 1296 | 13.3 | 1306 | 13.78 | 1315 | 14.26 | 1324 | 14.74 | 1333 | 15.22 | 1342 | 15.71 | 1359 | 16.7 | 1376 | 17.69 | 1393 | 18.7
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
8764 | 1400 | 759 | 3.57 | 820 | 4.38 | 889 | 5.34
9390 | 1500 | 779 | 3.89 | 837 | 4.73 | 896 | 5.65 | 959 | 6.68
10016 | 1600 | 801 | 4.23 | 855 | 5.12 | 908 | 6.03 | 966 | 7.04 | 1025 | 8.14
10642 | 1700 | 823 | 4.6 | 876 | 5.53 | 926 | 6.48 | 976 | 7.45 | 1032 | 8.55 | 1087 | 9.73 | 1140 | 10.93
11268 | 1800 | 846 | 4.99 | 897 | 5.96 | 946 | 6.96 | 994 | 7.97 | 1040 | 8.99 | 1094 | 10.19 | 1146 | 11.43 | 1196 | 12.69
11894 | 1900 | 871 | 5.4 | 919 | 6.42 | 967 | 7.46 | 1012 | 8.52 | 1058 | 9.58 | 1101 | 10.67 | 1153 | 11.94 | 1203 | 13.25 | 1251 | 14.58
12520 | 2000 | 896 | 5.84 | 942 | 6.91 | 989 | 7.99 | 1033 | 9.08 | 1076 | 10.2 | 1119 | 11.33 | 1159 | 12.47 | 1209 | 13.81 | 1257 | 15.18 | 1303 | 16.58
13772 | 2200 | 948 | 6.78 | 992 | 7.95 | 1034 | 9.13 | 1077 | 10.31 | 1118 | 11.51 | 1156 | 12.73 | 1196 | 13.96 | 1234 | 15.2 | 1271 | 16.45 | 1316 | 17.91
15024 | 2400 | 1001 | 7.85 | 1044 | 9.11 | 1084 | 10.38 | 1122 | 11.67 | 1161 | 12.96 | 1199 | 14.25 | 1236 | 15.57 | 1271 | 16.9 | 1307 | 18.24 | 1342 | 19.59
16276 | 2600 | 1056 | 9.05 | 1097 | 10.38 | 1136 | 11.76 | 1173 | 13.14 | 1208 | 14.52 | 1243 | 15.92 | 1279 | 17.31 | 1314 | 18.73 | 1347 | 20.16 | 1379 | 21.6
17528 | 2800 | 1113 | 10.4 | 1151 | 11.81 | 1188 | 13.26 | 1224 | 14.74 | 1258 | 16.23 | 1291 | 17.71 | 1323 | 19.22 | 1357 | 20.71 | 1390 | 22.21 | 1421 | 23.74
18780 | 3000 | 1171 | 11.91 | 1207 | 13.39 | 1242 | 14.92 | 1277 | 16.47 | 1310 | 18.06 | 1342 | 19.65 | 1373 | 21.24 | 1403 | 22.85 | 1434 | 24.45 | 1465 | 26.05
20032 | 3200 | 1230 | 13.59 | 1264 | 15.15 | 1297 | 16.75 | 1330 | 18.38 | 1362 | 20.04 | 1393 | 21.73 | 1423 | 23.44 | 1453 | 25.12 | 1481 | 26.82 | 1509 | 28.54
21284 | 3400 | 1289 | 15.45 | 1322 | 17.09 | 1354 | 18.77 | 1385 | 20.47 | 1416 | 22.21 | 1446 | 23.97 | 1475 | 25.76 | 1504 | 27.58 | 1532 | 29.35 | 1559 | 31.15
22536 | 3600 | 1349 | 17.5 | 1381 | 19.23 | 1412 | 20.98 | 1441 | 22.76 | 1470 | 24.56 | 1499 | 26.4 | 1528 | 28.27 | 1556 | 30.16 | 1583 | 32.07 | 1609 | 33.96
23788 | 3800 | 1409 | 19.71 | 1440 | 21.56 | 1470 | 23.39 | 1499 | 25.25 | 1526 | 27.13 | 1554 | 29.04 | 1581 | 30.98 | 1608 | 32.94 | 1635 | 34.93 | 1660 | 36.94
25040 | 4000 | 1470 | 22.06 | 1500 | 24.11 | 1529 | 26.02 | 1557 | 27.96 | 1584 | 29.91 | 1610 | 31.9 | 1635 | 33.9 | 1662 | 35.94 | 1688 | 38.01 | 1713 | 40.09
26292 | 4200 | 1531 | 24.62 | 1560 | 26.85 | 1588 | 28.88 | 1615 | 30.89 | 1641 | 32.92 | 1667 | 34.98 | 1691 | 37.06 | 1716 | 39.17 | 1741 | 41.31 | 1766 | 43.47
27544 | 4400 | 1592 | 27.39 | 1621 | 29.72 | 1648 | 31.97 | 1674 | 34.06 | 1700 | 36.17 | 1724 | 38.31 | 1748 | 40.47 | 1772 | 42.64 | 1795 | 44.84 | 1819 | 47.08
28796 | 4600 | 1654 | 30.4 | 1682 | 32.81 | 1708 | 35.26 | 1734 | 37.48 | 1758 | 39.67 | 1782 | 41.88 | 1806 | 44.12 | 1829 | 46.37 | 1851 | 48.64 | 1873 | 50.94
30048 | 4800 | 1716 | 33.64 | 1743 | 36.15 | 1769 | 38.68 | 1794 | 41.15 | 1818 | 43.42 | 1841 | 45.71 | 1864 | 48.03 | 1886 | 50.36 | 1908 | 52.71 | 1930 | 55.08
31300 | 5000 | 1779 | 37.14 | 1804 | 39.73 | 1829 | 42.36 | 1854 | 45.01 | 1877 | 47.45 | 1900 | 49.82 | 1922 | 52.21 | 1944 | 54.61 | 1966 | 57.04 | 1987 | 59.48
32552 | 5200 | 1841 | 40.89 | 1866 | 43.58 | 1891 | 46.29 | 1914 | 49.03 | 1937 | 51.75 | 1959 | 54.2 | 1981 | 56.67 | 2003 | 59.15 | 2023 | 61.65 | 2044 | 64.17
33804 | 5400 | 1904 | 44.91 | 1928 | 47.69 | 1952 | 50.49 | 1975 | 53.33 | 1998 | 56.18 | 2019 | 58.87 | 2041 | 61.42 | 2061 | 63.98 | 2082 | 66.56 | 2102 | 69.16
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
15024 | 2400 | 1376 | 20.95 | 1456 | 24.09 | 1534 | 27.38 | 1608 | 30.75
16276 | 2600 | 1413 | 23.05 | 1477 | 25.97 | 1547 | 29.22 | 1621 | 32.76 | 1691 | 36.36
17528 | 2800 | 1452 | 25.28 | 1513 | 28.38 | 1573 | 31.52 | 1634 | 34.82 | 1704 | 38.58 | 1771 | 42.41 | 1835 | 46.3
18780 | 3000 | 1495 | 27.66 | 1553 | 30.94 | 1609 | 34.26 | 1666 | 37.6 | 1720 | 40.99 | 1784 | 44.86 | 1848 | 48.91 | 1910 | 53.02 | 1969 | 57.19
20032 | 3200 | 1539 | 30.23 | 1596 | 33.66 | 1650 | 37.15 | 1702 | 40.69 | 1756 | 44.23 | 1807 | 47.81 | 1861 | 51.59 | 1922 | 55.86 | 1982 | 60.19 | 2039 | 64.57
21284 | 3400 | 1585 | 32.97 | 1639 | 36.58 | 1693 | 40.22 | 1744 | 43.92 | 1793 | 47.66 | 1844 | 51.41 | 1893 | 55.19 | 1940 | 59 | 1994 | 63.26 | 2052 | 67.8
22536 | 3600 | 1635 | 35.85 | 1685 | 39.69 | 1736 | 43.5 | 1787 | 47.34 | 1835 | 51.24 | 1881 | 55.19 | 1929 | 59.14 | 1976 | 63.11 | 2021 | 67.12 | 2066 | 71.17
23788 | 3800 | 1685 | 38.96 | 1735 | 42.93 | 1781 | 46.98 | 1830 | 50.99 | 1878 | 55.04 | 1924 | 59.13 | 1968 | 63.27 | 2012 | 67.44 | 2058 | 71.61 | 2101 | 75.8
25040 | 4000 | 1737 | 42.19 | 785 | 46.41 | 1831 | 50.6 | 1875 | 54.86 | 1922 | 59.07 | 1967 | 63.31 | 2011 | 67.6 | 2053 | 71.93 | 2095 | 76.31 | 2137 | 80.67
26292 | 4200 | 1790 | 45.65 | 1836 | 50.06 | 1881 | 54.46 | 1925 | 58.87 | 1967 | 63.33 | 2011 | 67.74 | 2054 | 72.18 | 2096 | 76.65 | 2137 | 81.18 | 2176 | 85.74
27544 | 4400 | 1843 | 49.33 | 1888 | 53.9 | 1932 | 58.54 | 1975 | 63.12 | 2016 | 67.73 | 2056 | 72.39 | 2098 | 77.01 | 2139 | 81.63 | 2180 | 66.3 | 2219 | 91.01
28796 | 4600 | 1896 | 53.27 | 1941 | 57.98 | 1984 | 62.77 | 2025 | 67.62 | 2066 | 72.39 | 2105 | 77.19 | 2144 | 82.06 | 2183 | 86.88 | 2223 | 91.69 | 2262 | 96.55
30048 | 4800 | 1951 | 57.46 | 1994 | 62.33 | 2036 | 67.26 | 2077 | 72.26 | 2116 | 77.32 | 2155 | 82.27 | 2193 | 87.27 | 2229 | 92.33 | 2267 | 97.37
31300 | 5000 | 2007 | 61.95 | 2048 | 66.94 | 2089 | 72.02 | 2129 | 77.17 | 2168 | 82.38 | 2206 | 87.63 | 2243 | 92.78 | 2279 | 97.97