## Sheet1
1
Single Width
| . |  | Single Inlet
120 THSB Centrifugal Blowers Single Width - Single Inlet Capacities
Intake Area = .92 Sq. Ft. Wheel Diameter =12" | [17 empty] | Class I
Outlet Area = .83 Sq. Ft . Tip Speed F.P.M = 3.21 * R.P.M | [17 empty] | Class II
Max B.H.P. =.05 (RPM/1000)³ | [17 empty] | Class III
C.F.M | VEL | 1/4 SP |  | 3/8SP |  | 1/2SP |  | 5/8SP |  | 3/4SP |  | 7/8SP |  | 1SP |  | 1-1/4SP |  | 1-1/2SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
688 | 800 | 1016 | .06 | 1102 | .07 | 1179 | .09 | 1253 | .11 | 1323 | .13 | 1389 | .15 | 1452 | .17 | 1588 | .21 | 1725 | .27
774 | 900 | 1098 | .07 | 1180 | .09 | 1254 | .11 | 1322 | .13 | 1388 | .15 | 1452 | .17 | 1513 | .19 | 1626 | .23 | 1748 | .29
860 | 1000 | 1182 | .09 | 1260 | .11 | 1332 | .13 | 1397 | .15 | 1459 | .17 | 1518 | .19 | 1577 | .22 | 1687 | .26 | 1788 | .31
946 | 1100 | 1268 | .11 | 1343 | .13 | 1411 | .16 | 1475 | .18 | 1534 | .20 | 1590 | .22 | 1644 | .25 | 1752 | .30 | 1851 | .35
1032 | 1200 | 1352 | .13 | 1427 | .15 | 1492 | .18 | 1554 | .21 | 1612 | .23 | 1666 | .26 | 1718 | .28 | 1818 | .33 | 1916 | .39
1118 | 1300 | 1411 | .15 | 1512 | .18 | 1575 | .21 | 1634 | .24 | 1690 | .27 | 1744 | .29 | 1794 | .32 | 1890 | .37 | 1981 | .43
1204 | 1400 | 1471 | .17 | 1599 | .21 | 1660 | .24 | 1717 | .28 | 1771 | .31 | 1823 | .34 | 1872 | .36 | 1965 | .42 | 2052 | .48
1290 | 1500 | 1543 | .20 | 1674 | .24 | 1745 | .28 | 1800 | .31 | 1853 | .35 | 1903 | .38 | 1951 | .41 | 2042 | .47 | 2127 | .53
1376 | 1600 | 1630 | .23 | 1733 | .28 | 1832 | .32 | 1885 | .35 | 1936 | .39 | 1984 | .43 | 2031 | .46 | 2120 | .53 | 2204 | .59
1462 | 1700 | 1718 | .27 | 1793 | .31 | 1914 | .36 | 1971 | .40 | 2020 | .44 | 2067 | .48 | 2113 | .52 | 2200 | .59 | 2281 | .66
1548 | 1800 | 1806 | .32 | 1858 | .35 | 1973 | .40 | 2058 | .45 | 2105 | .49 | 2151 | .53 | 2196 | .57 | 2280 | .66 | 2360 | .73
1634 | 1900 | 1895 | .36 | 1945 | .40 | 2032 | .45 | 2140 | .51 | 2192 | .55 | 2236 | .59 | 2279 | .63 | 2362 | .72 | 2440 | .81
1720 | 2000 | 1984 | .42 | 2032 | .45 | 2093 | .50 | 2198 | .56 | 2279 | .61 | 2322 | .66 | 2364 | .70 | 2444 | .79 | 2520 | .88
1892 | 2200 | 2163 | .54 | 2208 | .58 | 2251 | .62 | 2318 | .67 | 2413 | .74 | 2496 | .80 | 2536 | .85 | 2612 | .95 | 2685 | 1.05
2064 | 2400 | 2344 | .68 | 2385 | .72 | 2425 | .77 | 2464 | .81 | 2533 | .87 | 2621 | .95 | 2704 | 1.02 | 2783 | 1.13 | 2853 | 1.24
2236 | 2600 | 2525 | .85 | 2564 | .89 | 2602 | .94 | 2639 | .99 | 2674 | 1.04 | 2740 | 1.11 | 2822 | 1.19 | 2957 | 1.34 | 3024 | 1.45
2408 | 2800 | 2708 | 1.04 | 2744 | 1.09 | 2780 | 1.14 | 2814 | 1.20 | 2848 | 1.25 | 2881 | 1.30 | 2942 | 1.37 | 3092 | 1.55 | 3197 | 1.70
2580 | 3000 | 2891 | 1.27 | 2925 | 1.32 | 2959 | 1.38 | 2992 | 1.43 | 3024 | 1.49 | 3055 | 1.54 | 3086 | 1.60 | 3211 | 1.77 | 3347 | 1.95
2752 | 3200 | 3075 | 1.52 | 3107 | 1.58 | 3139 | 1.64 | 3170 | 1.70 | 3200 | 1.75 | 3230 | 1.81 | 3260 | 1.87 | 3331 | 2.01 | 3466 | 2.20
2924 | 3400 | 3259 | 1.81 | 3290 | 1.87 | 3320 | 1.93 | 3349 | 1.99 | 3378 | 2.06 | 3407 | 2.12 | 3435 | 2.18 | 3490 | 2.31 | 3585 | 2.48
C.F.M | VEL | 2 SP |  | 2-1/2SP |  | 3SP |  | 3-1/2SP |  | 4SP |  | 4-1/2SP |  | 5SP |  | 5-1/2SP |  | 6SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1032 | 1200 | 2093 | .50 | 2271 | .63 | 2452 | .78 | 2631 | .95
1118 | 1300 | 2157 | .55 | 2314 | .68 | 2482 | .82 | 2649 | .99 | 2816 | 1.16
1204 | 1400 | 2221 | .60 | 2377 | .74 | 2520 | .87 | 2679 | 1.03 | 2834 | 1.21 | 2990 | 1.40
1290 | 1500 | 2287 | .66 | 2441 | .80 | 2582 | .94 | 2717 | 1.09 | 2865 | 1.27 | 3009 | 1.45 | 3156 | 1.65
1376 | 1600 | 2357 | .73 | 2506 | .87 | 2646 | 1.02 | 2777 | 1.17 | 2904 | 1.33 | 3042 | 1.52 | 3175 | 1.71 | 3315 | 1.92
1462 | 1700 | 2432 | .80 | 2572 | .94 | 2711 | 1.10 | 2840 | 1.26 | 2962 | 1.42 | 3081 | 1.59 | 3212 | 1.79 | 3337 | 1.99 | 3465 | 2.21
1548 | 1800 | 2508 | .88 | 2644 | 1.03 | 2776 | 1.18 | 2904 | 1.35 | 3025 | 1.52 | 3139 | 1.6 | 3251 | 1.87 | 3375 | 2.08 | 3495 | 2.29
1634 | 1900 | 2585 | .96 | 2718 | 1.11 | 2843 | 1.27 | 2970 | 1.45 | 3089 | 1.62 | 3203 | 1.80 | 3311 | 1.98 | 3414 | 2.17 | 3533 | 2.69
1720 | 2000 | 2663 | 1.05 | 2794 | 1.21 | 2917 | 1.38 | 306 | 1.55 | 3154 | 1.73 | 3267 | 1.92 | 3374 | 2.10 | 3477 | 2.30 | 3576 | 2.49
1892 | 2200 | 2822 | 1.25 | 2949 | 1.42 | 3068 | 1.60 | 3180 | 1.78 | 3287 | 1.97 | 3397 | 2.17 | 3503 | 2.37 | 3604 | 2.57 | 3702 | 2.78
2064 | 2400 | 2984 | 1.46 | 3107 | 1.66 | 3223 | 1.86 | 3332 | 2.05 | 3436 | 2.25 | 3535 | 2.45 | 3635 | 2.66 | 3734 | 2.88 | 3831 | 3.10
2236 | 2600 | 3150 | 1.69 | 3268 | 1.93 | 3380 | 2.14 | 3487 | 2.35 | 3588 | 2.56 | 3686 | 2.78 | 3779 | 2.99 | 3869 | 3.21 | 3962 | 3.44
2408 | 2800 | 3319 | 1.95 | 3433 | 2.20 | 3541 | 2.46 | 3645 | 2.69 | 3744 | 2.91 | 3839 | 3.14 | 3930 | 3.37 | 4018 | 3.60 | 4104 | 3.83
2580 | 3000 | 3490 | 2.23 | 3600 | 2.50 | 3705 | 2.78 | 3804 | 3.06 | 3901 | 3.29 | 3994 | 3.53 | 4084 | 3.78 | 4170 | 4.02 | 4254 | 4.27
2752 | 3200 | 3663 | 2.56 | 3770 | 2.84 | 3871 | 3.13 | 3968 | 3.42 | 4062 | 3.72 | 4152 | 3.97 | 4240 | 4.23 | 4325 | 4.49 | 4407 | 4.75
2924 | 3400 | 3828 | 2.90 | 3941 | 3.21 | 4040 | 3.51 | 4134 | 3.82 | 4225 | 4.13 | 4313 | 4.45 | 4399 | 4.72 | 4481 | 4.99 | 4562 | 5.27
3096 | 3600 | 3945 | 3.23 | 4115 | 3.62 | 4210 | 3.94 | 4302 | 4.26 | 4391 | 4.59 | 4476 | 4.92 | 4559 | 5.25 | 4640 | 5.54 | 4719 | 5.83
3268 | 3800 | 4064 | 3.58 | 4279 | 4.05 | 4383 | 4.40 | 4472 | 4.74 | 4558 | 5.08 | 4642 | 5.42 | 4723 | 5.77 | 4802 | 6.13 | 4879 | 6.44
3440 | 4000 | 4185 | 3.96 | 4396 | 4.46 | 4557 | 4.90 | 4643 | 5.25 | 4727 | 5.61 | 4809 | 5.97 | 4888 | 6.34 | 4965 | 6.70 | 5040 | 7.07
C.F.M | VEL | 6-1/2 SP |  | 7SP |  | 7-1/2SP |  | 8SP |  | 9SP |  | 10SP |  | 11SP |  | 12SP |  | 13SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1892 | 2200 | 3796 | 2.99 | 3887 | 3.20 | 3979 | 3.43 | 4082 | 3.68 | 4278 | 4.20 | 4478 | 4.76 | 4677 | 5.36 | 4867 | 5.98 | 5050 | 6.61
2064 | 2400 | 3924 | 3.32 | 4014 | 3.55 | 4101 | 3.77 | 4186 | 4.01 | 4355 | 4.49 | 4541 | 5.05 | 4718 | 5.62 | 4904 | 6.25 | 5086 | 6.90
2236 | 2600 | 4054 | 3.68 | 4143 | 3.92 | 4229 | 4.16 | 4313 | 4.40 | 4474 | 4.90 | 4627 | 5.40 | 4794 | 5.97 | 4963 | 6.58 | 5125 | 7.20
2408 | 2800 | 4186 | 4.07 | 4274 | 4.32 | 4359 | 4.57 | 4442 | 4.83 | 4601 | 5.35 | 4753 | 5.88 | 4899 | 6.42 | 5040 | 6.97 | 5202 | 7.62
2580 | 3000 | 4335 | 4.52 | 4414 | 4.77 | 4492 | 5.03 | 4574 | 5.30 | 4731 | 5.84 | 4881 | 6.39 | 5026 | 6.96 | 5164 | 7.53 | 5298 | 8.11
2752 | 3200 | 4487 | 5.01 | 4564 | 5.27 | 4640 | 5.54 | 4714 | 5.81 | 4863 | 6.37 | 5012 | 6.95 | 5154 | 7.54 | 5292 | 8.14 | 5424 | 8.74
2924 | 3400 | 4640 | 5.54 | 4716 | 5.82 | 4791 | 6.10 | 4863 | 6.38 | 5004 | 6.95 | 5144 | 7.54 | 5285 | 8.15 | 5421 | 8.78 | 5552 | 9.41
3096 | 3600 | 4796 | 6.12 | 4871 | 6.41 | 4944 | 6.70 | 5015 | 7.00 | 5154 | 7.59 | 5287 | 8.20 | 5418 | 8.81 | 5552 | 9.46 | 5682 | 10.12
3268 | 3800 | 4954 | 5.75 | 5027 | 7.05 | 5099 | 7.36 | 5169 | 7.66 | 5306 | 8.29 | 5436 | 8.91 | 5563 | 9.55 | 5685 | 10.19 | 5814 | 10.87
3440 | 4000 | 5114 | 7.42 | 5186 | 7.74 | 5256 | 8.06 | 5325 | 8.38 | 5459 | 9.02 | 5588 | 9.68 | 5713 | 10.34 | 5833 | 11.01
3612 | 4200 | 5276 | 8.10 | 5346 | 8.48 | 5416 | 8.82 | 5483 | 9.15 | 5615 | 9.82 | 5742 | 10.50 | 5865 | 11.19
3784 | 4400 | 5440 | 8.80 | 5509 | 9.20 | 5577 | 9.62 | 5643 | 9.97 | 5773 | 10.68 | 5897 | 11.38
3946 | 4600 | 5606 | 9.54 | 5673 | 9.96 | 5740 | 10.39 | 5805 | 10.82 | 5932 | 11.58
4128 | 4800 | 5773 | 10.33 | 5839 | 10.77 | 5904 | 11.21 | 5968 | 11.65
4300 | 5000 | 5942 | 11.18 | 6007 | 11.63 | 6071 | 12.09
4472 | 5200 | 6112 | 12.08 | 6176 | 12.55