## Sheet1
AIRFOIL BLADE
SIZE S - AF - 24 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 24½inches 622 mm | [13 empty] | SIZE .24 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 6.41 feet 1.954 m | [13 empty] | CLASS I |  | 1782
Inlet Diameter / Area 27 3/16 inches Dia/3.98 sq f.t 691mm /.3697 m² | [13 empty] | CLASS II |  | 2325
Outlet Size Area 25 11/16 *19 5/16Inches I.D/3.46 sq.ft 652*491mm/.3214 m² | [13 empty] | CLASS III |  | 2929
Tip Speed 6.41 * rpm ft./minute 1.954*RPM m/minute | [13 empty] | CLASS IV |  | 3222
Maximum BHP 1.80*(RPM÷1000)³ BHP 1.342 * (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
2076 | 600 | 412 | 0.12 | 461 | 0.17 | 507 | 0.23 | 550 | 0.28
2422 | 700 | 447 | 0.16 | 493 | 0.21 | 534 | 0.27 | 573 | 0.33 | 612 | 0.39 | 648 | 0.45
2768 | 800 | 486 | 0.2 | 526 | 0.26 | 566 | 0.32 | 603 | 0.39 | 636 | 0.46 | 672 | 0.53 | 705 | 0.59 | 766 | 0.73
3114 | 900 | 525 | 0.24 | 564 | 0.31 | 599 | 0.38 | 635 | 0.46 | 668 | 0.53 | 698 | 0.61 | 729 | 0.68 | 789 | 0.83 | 844 | 0.99
3460 | 1000 | 565 | 0.3 | 602 | 0.37 | 536 | 0.45 | 668 | 0.53 | 700 | 0.61 | 730 | 0.69 | 758 | 0.78 | 813 | 0.95 | 868 | 1.12 | 918 | 1.29
3806 | 1100 | 606 | 0.36 | 642 | 0.44 | 674 | 0.53 | 704 | 0.62 | 733 | 0.7 | 763 | 0.79 | 790 | 0.88 | 842 | 1.07 | 892 | 1.25 | 942 | 1.44
4152 | 1200 | 648 | 0.43 | 682 | 0.52 | 713 | 0.62 | 742 | 0.71 | 770 | 0.8 | 796 | 0.9 | 823 | 1 | 874 | 1.19 | 921 | 1.39 | 966 | 1.6
4498 | 1300 | 690 | 0.51 | 723 | 0.61 | 753 | 0.71 | 781 | 0.82 | 808 | 0.92 | 833 | 1.02 | 857 | 1.12 | 906 | 1.33 | 953 | 1.54 | 996 | 1.76
4844 | 1400 | 733 | 0.6 | 764 | 0.71 | 793 | 0.82 | 821 | 0.93 | 846 | 1.04 | 781 | 1.15 | 894 | 1.26 | 939 | 1.48 | 958 | 1.71 | 1027 | 1.94
5190 | 1500 | 776 | 0.71 | 806 | 0.82 | 834 | 0.94 | 860 | 1.06 | 885 | 1.18 | 909 | 1.29 | 932 | 1.41 | 975 | 1.64 | 1018 | 1.88 | 1060 | 2.13
5536 | 1600 | 820 | 0.83 | 849 | 0.95 | 875 | 1.07 | 901 | 1.19 | 925 | 1.32 | 948 | 1.45 | 971 | 1.57 | 1013 | 1.82 | 1052 | 2.08 | 1092 | 2.33
5882 | 1700 | 864 | 0.96 | 891 | 1.08 | 917 | 1.21 | 942 | 1.35 | 965 | 1.48 | 988 | 1.61 | 1010 | 1.75 | 1051 | 2.01 | 1089 | 2.28 | 1126 | 2.55
6228 | 1800 | 909 | 1.1 | 935 | 1.24 | 960 | 1.37 | 983 | 1.51 | 1006 | 1.65 | 1028 | 1.79 | 1049 | 1.94 | 1089 | 2.22 | 1127 | 2.5 | 1163 | 2.78
6574 | 1900 | 954 | 1.26 | 978 | 1.41 | 1002 | 1.55 | 1025 | 1.69 | 1047 | 1.84 | 1069 | 1.99 | 1089 | 2.14 | 1128 | 2.45 | 1165 | 2.74 | 1200 | 3.03
6920 | 2000 | 999 | 1.44 | 1022 | 1.59 | 1045 | 1.74 | 1067 | 1.89 | 1089 | 2.05 | 1110 | 2.2 | 1130 | 2.36 | 1168 | 2.68 | 1204 | 2.99 | 1238 | 3.3
7612 | 2200 | 1090 | 1.84 | 1111 | 2.01 | 1132 | 2.18 | 1153 | 2.35 | 1173 | 2.51 | 1193 | 2.68 | 1212 | 2.85 | 1248 | 3.19 | 1283 | 3.55 | 1316 | 3.89
8304 | 2400 | 1181 | 2.32 | 1201 | 2.5 | 1220 | 2.69 | 1240 | 2.88 | 1259 | 3.05 | 1277 | 3.24 | 1295 | 3.42 | 1330 | 3.79 | 133 | 4.17 | 1395 | 4.55
8996 | 2600 | 1273 | 2.88 | 1292 | 3.08 | 1310 | 3.28 | 1327 | 3.49 | 1345 | 3.68 | 1363 | 3.87 | 1380 | 4.07 | 1413 | 4.47 | 1444 | 4.87 | 1475 | 5.28
9688 | 2800 | 1366 | 3.52 | 1383 | 3.74 | 1400 | 3.96 | 1416 | 4.18 | 1433 | 4.4 | 1449 | 4.61 | 1465 | 4.81 | 1497 | 5.24 | 1527 | 5.66 | 1557 | 6.1
10380 | 3000 | 1458 | 4.27 | 1474 | 4.5 | 1490 | 4.73 | 1506 | 4.96 | 1521 | 5.2 | 1537 | 5.43 | 1552 | 5.66 | 1582 | 6.1 | 1611 | 6.56 | 1639 | 7.02
11072 | 3200 | 1551 | 5.11 | 1566 | 5.36 | 1582 | 5.6 | 1596 | 5.85 | 611 | 6.1 | 1625 | 6.36 | 1639 | 6.6 | 1668 | 7.08 | 1696 | 7.56 | 1723 | 8.04
11764 | 3400 | 1644 | 6.06 | 1659 | 6.32 | 1673 | 6.58 | 1687 | 6.85 | 1701 | 7.11 | 1714 | 7.38 | 1728 | 7.65 | 1755 | 8.16 | 1782 | 8.67 | 1807 | 9.18
12456 | 3600 | 1738 | 7.13 | 1751 | 7.4 | 1765 | 7.68 | 1778 | 7.96 | 1791 | 8.24 | 1804 | 8.52 | 1817 | 8.8 | 1842 | 9.36 | 1868 | 9.9 | 1893 | 10.43
13148 | 3800 | 1831 | 8.32 | 1844 | 8.61 | 1857 | 8.9 | 1870 | 9.19 | 1882 | 9.49 | 1895 | 9.78 | 1907 | 10.08 | 1931 | 10.68 | 1955 | 11.25 | 1979 | 11.81
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
4498 | 1300 | 1037 | 1.99 | 1122 | 2.42 | 1199 | 2.86
4844 | 1400 | 1067 | 2.17 | 1146 | 2.65 | 1223 | 3.11 | 1294 | 3.59
5190 | 1500 | 1099 | 2.37 | 1173 | 2.88 | 1247 | 3.38 | 1317 | 3.89 | 1384 | 4.39 | 1450 | 4.97
5536 | 1600 | 1132 | 2.59 | 1204 | 3.12 | 1271 | 3.67 | 1341 | 4.2 | 1407 | 4.73 | 1469 | 5.28 | 1530 | 5.85
5882 | 1700 | 1164 | 2.82 | 1236 | 3.38 | 1302 | 3.95 | 1365 | 4.53 | 1431 | 5.09 | 1493 | 5.66 | 1552 | 6.23 | 1608 | 6.81
6228 | 1800 | 1198 | 3.07 | 1268 | 3.65 | 1334 | 4.24 | 1395 | 4.85 | 1455 | 5.46 | 1517 | 6.06 | 1575 | 6.66 | 1631 | 7.26 | 1684 | 7.88 | 1742 | 8.62
6574 | 1900 | 1234 | 3.33 | 1301 | 3.94 | 1366 | 4.56 | 1426 | 5.19 | 1483 | 5.84 | 1541 | 6.48 | 1599 | 7.1 | 1654 | 7.74 | 1708 | 8.37 | 1759 | 9.02
6920 | 2000 | 1271 | 3.61 | 1334 | 4.25 | 1398 | 4.89 | 1458 | 5.55 | 1514 | 6.22 | 1568 | 6.9 | 1623 | 7.57 | 1678 | 8.23 | 1731 | 8.89 | 1782 | 9.56
7612 | 2200 | 1347 | 4.23 | 1407 | 4.92 | 1464 | 5.62 | 1523 | 6.32 | 1578 | 7.04 | 1631 | 7.76 | 1681 | 8.51 | 1729 | 9.26 | 1779 | 9.99 | 1830 | 10.71
8304 | 2400 | 1425 | 4.93 | 1483 | 5.67 | 1537 | 6.42 | 1589 | 7.18 | 1643 | 7.95 | 1695 | 8.72 | 1744 | 9.51 | 1791 | 10.3 | 1837 | 11.11 | 1881 | 11.94
8996 | 2600 | 1504 | 5.69 | 1560 | 6.51 | 1613 | 7.31 | 1663 | 8.12 | 1710 | 8.95 | 1760 | 9.77 | 1809 | 10.6 | 1855 | 11.45 | 1900 | 12.3 | 1944 | 13.17
9688 | 2800 | 1585 | 6.54 | 1639 | 7.43 | 1690 | 8.3 | 1738 | 9.16 | 1785 | 10.03 | 1829 | 10.92 | 1875 | 11.81 | 1920 | 12.7 | 1965 | 13.6 | 2007 | 14.51
10380 | 3000 | 1666 | 7.48 | 1719 | 8.43 | 1768 | 9.39 | 1815 | 10.31 | 1860 | 11.23 | 1904 | 12.16 | 1946 | 13.11 | 1987 | 14.06 | 2030 | 15.01 | 2072 | 15.96
11072 | 3200 | 1749 | 8.53 | 1800 | 9.53 | 1848 | 10.54 | 1894 | 11.57 | 1937 | 12.54 | 1980 | 13.51 | 2020 | 14.51 | 2060 | 15.51 | 2098 | 16.53 | 2138 | 17.54
11764 | 3400 | 1833 | 9.69 | 1881 | 10.74 | 1928 | 11.8 | 1972 | 12.88 | 2015 | 13.97 | 2056 | 15 | 2096 | 16.03 | 2135 | 17.08 | 2172 | 18.14 | 2209 | 19.22
12456 | 3600 | 1917 | 10.97 | 1964 | 12.07 | 2009 | 13.18 | 2052 | 14.31 | 2094 | 15.46 | 2134 | 16.61 | 2173 | 17.69 | 2211 | 18.79 | 2247 | 18.89 | 2283 | 21.01
13148 | 3800 | 2002 | 12.38 | 2048 | 13.53 | 2091 | 14.69 | 2133 | 15.87 | 2174 | 17.07 | 2213 | 18.28 | 2251 | 19.49 | 2288 | 20.63 | 2324 | 21.78 | 2359 | 22.95
13840 | 4000 | 2088 | 13.92 | 2132 | 15.12 | 2174 | 16.33 | 2215 | 17.56 | 2255 | 18.81 | 2293 | 20.07 | 2330 | 21.34 | 2366 | 22.62 | 2401 | 23.82 | 2435 | 25.03
14532 | 4200 | 2175 | 15.6 | 2217 | 16.85 | 2258 | 18.12 | 2298 | 19.4 | 2336 | 20.69 | 2373 | 22 | 2410 | 23.32 | 2445 | 24.66 | 2479 | 26.01 | 2513 | 27.27
15224 | 4400 | 2262 | 17.43 | 2303 | 18.73 | 2343 | 20.04 | 2381 | 21.38 | 2418 | 22.72 | 2455 | 24.08 | 2490 | 25.45 | 2524 | 26.84 | 2558 | 28.23 | 2591 | 29.65
15916 | 4600 | 2350 | 19.41 | 2389 | 20.76 | 2428 | 22.13 | 2465 | 23.51 | 2501 | 24.9 | 2537 | 26.31 | 2571 | 27.73 | 2605 | 29.17 | 2637 | 30.61 | 2670 | 32.07
16608 | 4800 | 2438 | 21.52 | 2476 | 22.95 | 2513 | 24.37 | 2550 | 25.8 | 2585 | 27.25 | 2619 | 28.71 | 2653 | 30.18 | 2686 | 31.66 | 2718 | 33.16 | 2749 | 34.66
17300 | 5000 | 2527 | 23.78 | 2564 | 25.31 | 2600 | 26.78 | 2635 | 28.27 | 2669 | 29.76 | 2703 | 31.27 | 2735 | 32.79 | 2767 | 34.32 | 2799 | 35.87 | 2829 | 37.42
17992 | 5200 | 2617 | 26.21 | 2651 | 27.85 | 2686 | 29.37 | 2721 | 30.90 | 2754 | 32.45 | 2787 | 34.01 | 2818 | 35.58 | 2850 | 37.16 | 2880 | 38.75 | 2910 | 40.35
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
7612 | 2200 | 1879 | 11.44 | 1971 | 12.91 | 2059 | 14.4
8304 | 2400 | 1926 | 12.74 | 2019 | 14.31 | 2106 | 15.9 | 2188 | 17.52 | 2266 | 19.15
8996 | 2600 | 1985 | 14.04 | 2067 | 15.82 | 2153 | 17.51 | 2235 | 19.22 | 2313 | 20.95 | 2388 | 22.7 | 2460 | 24.5
9688 | 2800 | 2049 | 15.43 | 2128 | 17.3 | 2203 | 19.21 | 2283 | 21.04 | 2360 | 22.87 | 2434 | 24.72 | 2506 | 26.58 | 2574 | 28.46 | 2641 | 30.36
10380 | 3000 | 2113 | 16.93 | 2191 | 18.89 | 2265 | 20.88 | 2336 | 22.92 | 2408 | 24.91 | 2482 | 26.86 | 2553 | 28.82 | 2621 | 30.8 | 2687 | 32.79 | 2751 | 34.8
11072 | 3200 | 2178 | 18.55 | 2255 | 20.6 | 2328 | 22.68 | 2398 | 24.8 | 2465 | 26.96 | 2530 | 29.13 | 2600 | 31.2 | 2668 | 33.27 | 2734 | 35.37 | 2798 | 37.47
11764 | 3400 | 2245 | 20.3 | 2320 | 22.44 | 2392 | 24.61 | 2461 | 26.82 | 2527 | 29.06 | 2591 | 31.33 | 2652 | 33.63 | 2716 | 35.88 | 2781 | 38.07 | 2845 | 40.28
12456 | 3600 | 2318 | 22.14 | 2386 | 24.42 | 2458 | 26.68 | 2526 | 28.98 | 2591 | 31.31 | 2654 | 33.67 | 2714 | 36.05 | 2773 | 38.47 | 2830 | 40.91 | 2892 | 43.23
13148 | 3800 | 2393 | 24.12 | 2458 | 26.5 | 2524 | 28.9 | 2591 | 31.28 | 2655 | 33.7 | 2717 | 36.15 | 2777 | 38.62 | 2835 | 41.12 | 2892 | 43.65 | 2946 | 46.21
13840 | 4000 | 2468 | 26.25 | 2533 | 28.72 | 2594 | 31.22 | 2657 | 33.74 | 2720 | 36.25 | 2782 | 38.78 | 2841 | 41.34 | 2898 | 43.93 | 2954 | 46.55 | 3008 | 49.19
14532 | 4200 | 2545 | 28.53 | 2608 | 31.09 | 2669 | 33.68 | 2727 | 36.32 | 2786 | 38.95 | 2847 | 41.58 | 2905 | 44.23 | 2962 | 46.9 | 3017 | 49.61 | 3071 | 52.33
15224 | 4400 | 2623 | 30.98 | 2684 | 33.62 | 2744 | 36.31 | 2801 | 39.03 | 2857 | 41.78 | 2913 | 44.54 | 2971 | 47.28 | 3027 | 50.04 | 3081 | 52.83 | 3134 | 55.65
15916 | 4600 | 2701 | 33.54 | 2762 | 36.33 | 2820 | 39.1 | 2876 | 41.91 | 2931 | 44.75 | 2983 | 47.63 | 3037 | 50.51 | 3092 | 53.36 | 3146 | 56.24 | 3198 | 59.14
16608 | 4800 | 2780 | 36.18 | 2839 | 39.21 | 2897 | 42.08 | 2952 | 44.98 | 3005 | 47.9 | 3057 | 50.87 | 3108 | 53.86 | 3158 | 56.86 | 3211 | 59.83