## Sheet1
AIRFOIL BLADE
SIZE S - AF - 30 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 30inches 762 mm | [13 empty] | SIZE 30 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 7.85 feet 2.393 m | [13 empty] | CLASS I |  | 1391
Inlet Diameter / Area 32 11/16 inches Dia/5.76 sq f.t 830mm /.5351 m² | [13 empty] | CLASS II |  | 1818
Outlet Size Area 23 7/16*31 ½Inches I.D/5.13 sq.ft 595*800mm/.4766 m² | [13 empty] | CLASS III |  | 2291
Tip Speed 7.85 * rpm ft./minute 2.393*RPM m/minute | [13 empty] | CLASS IV |  | 2520
Maximum BHP 5.15*(RPM÷1000)³ BHP 3.840* (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
3078 | 600 | 319 | 0.17 | 360 | 0.23 | 401 | 0.31
3591 | 700 | 345 | 0.21 | 382 | 0.29 | 417 | 0.37 | 451 | 0.45 | 489 | 0.55
4104 | 800 | 374 | 0.26 | 407 | 0.34 | 439 | 0.43 | 469 | 0.52 | 499 | 0.62 | 531 | 0.72 | 564 | 0.84
4617 | 900 | 403 | 0.31 | 435 | 0.41 | 464 | 0.51 | 492 | 0.61 | 519 | 0.71 | 546 | 0.62 | 571 | 0.92 | 631 | 1.18
5130 | 1000 | 434 | 0.38 | 463 | 0.49 | 491 | 0.6 | 517 | 0.71 | 543 | 0.82 | 567 | 0.93 | 591 | 1.05 | 638 | 1.28 | 692 | 1.56
5643 | 1100 | 466 | 0.46 | 493 | 0.57 | 519 | 0.69 | 544 | 0.81 | 567 | 0.93 | 591 | 1.06 | 614 | 1.18 | 657 | 1.43 | 699 | 1.69 | 749 | 2
6156 | 1200 | 498 | 0.55 | 524 | 0.67 | 548 | 0.8 | 572 | 0.93 | 594 | 1.06 | 616 | 1.19 | 637 | 1.33 | 679 | 1.6 | 719 | 1.87 | 757 | 2.15
6669 | 1300 | 531 | 0.66 | 555 | 0.79 | 578 | 0.9 | 601 | 1.06 | 622 | 1.2 | 643 | 1.34 | 663 | 1.49 | 703 | 1.77 | 740 | 2.07 | 777 | 2.37
7182 | 1400 | 564 | 0.78 | 587 | 0.92 | 609 | 1.06 | 630 | 1.2 | 651 | 1.35 | 671 | 1.51 | 690 | 1.66 | 727 | 1.97 | 764 | 2.28 | 798 | 2.6
7695 | 1500 | 597 | 0.9 | 620 | 1.06 | 641 | 1.21 | 661 | 1.37 | 680 | 1.52 | 700 | 1.68 | 718 | 1.85 | 753 | 2.18 | 788 | 2.51 | 822 | 2.84
8208 | 1600 | 631 | 1.05 | 652 | 1.22 | 673 | 1.38 | 692 | 1.54 | 710 | 1.71 | 729 | 1.88 | 747 | 2.05 | 781 | 2.4 | 814 | 2.75 | 846 | 3.1
8721 | 1700 | 664 | 1.21 | 685 | 1.4 | 705 | 1.57 | 724 | 1.74 | 741 | 1.91 | 759 | 2.09 | 776 | 2.27 | 809 | 2.64 | 841 | 3.01 | 871 | 3.38
9234 | 1800 | 699 | 1.39 | 719 | 1.59 | 738 | 1.78 | 756 | 1.96 | 773 | 2.14 | 789 | 2.32 | 806 | 2.51 | 838 | 2.89 | 869 | 3.29 | 898 | 3.68
9747 | 1900 | 733 | 1.59 | 752 | 1.8 | 771 | 2 | 788 | 2.19 | 805 | 2.38 | 821 | 2.57 | 836 | 2.77 | 867 | 3.17 | 897 | 3.58 | 926 | 3.99
10260 | 2000 | 767 | 1.81 | 786 | 2.02 | 804 | 2.24 | 821 | 2.45 | 837 | 2.65 | 852 | 2.85 | 868 | 3.05 | 897 | 3.47 | 926 | 3.89 | 954 | 4.33
11286 | 2200 | 837 | 2.31 | 854 | 2.54 | 870 | 2.78 | 886 | 3.02 | 902 | 3.25 | 917 | 3.47 | 931 | 3.69 | 958 | 4.13 | 985 | 4.59 | 1012 | 5.05
12312 | 2400 | 907 | 2.1 | 923 | 3.16 | 938 | 3.41 | 953 | 3.67 | 968 | 3.93 | 982 | 4.19 | 995 | 4.42 | 1022 | 4.9 | 1047 | 5.39 | 1071 | 5.88
13338 | 2600 | 977 | 3.6 | 992 | 3.87 | 1006 | 4.15 | 1021 | 4.42 | 1034 | 4.71 | 1048 | 4.99 | 1061 | 5.27 | 1086 | 5.78 | 1110 | 6.3 | 1133 | 6.83
14364 | 2800 | 1048 | 4.4 | 1062 | 4.69 | 1075 | 4.99 | 1089 | 5.29 | 1102 | 5.59 | 1114 | 5.89 | 1127 | 6.19 | 1151 | 6.78 | 1174 | 7.33 | 1196 | 7.89
15390 | 3000 | 1118 | 5.32 | 1132 | 5.63 | 1144 | 5.95 | 1157 | 6.26 | 1169 | 6.58 | 1181 | 6.91 | 1193 | 7.23 | 1216 | 7.89 | 1238 | 8.48 | 1260 | 9.08
14364 | 3200 | 1190 | 6.37 | 1202 | 6.7 | 1214 | 7.03 | 1226 | 7.37 | 1238 | 7.71 | 1249 | 8.05 | 1260 | 8.39 | 1282 | 9.09 | 1304 | 9.78 | 1324 | 10.4
15390 | 3400 | 1261 | 7.55 | 1273 | 7.9 | 1284 | 8.25 | 1295 | 8.61 | 1306 | 8.96 | 1317 | 9.32 | 1328 | 9.69 | 1349 | 10.42 | 1370 | 11.16 | 1389 | 11.87
16416 | 3600 | 1332 | 8.87 | 1343 | 9.24 | 1354 | 9.61 | 1365 | 9.99 | 1376 | 10.36 | 1386 | 10.74 | 1396 | 11.13 | 1416 | 11.89 | 1436 | 12.67 | 1455 | 13.46
17442 | 3800 | 1404 | 10.35 | 1414 | 10.73 | 1425 | 11.13 | 1435 | 11.52 | 1445 | 11.92 | 1455 | 12.31 | 1465 | 12.71 | 1484 | 13.2 | 1503 | 14.34 | 1521 | 15.16
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
7182 | 1400 | 833 | 2.92 | 901 | 3.59 | 977 | 4.38
7695 | 1500 | 854 | 3.18 | 918 | 3.87 | 984 | 4.63 | 1054 | 5.48
8208 | 1600 | 878 | 3.46 | 938 | 4.19 | 996 | 4.93 | 1061 | 5.78 | 1127 | 6.68
8721 | 1700 | 902 | 3.76 | 960 | 4.52 | 1016 | 5.3 | 1070 | 6.09 | 1134 | 7.02 | 1195 | 7.98
9234 | 1800 | 926 | 4.08 | 984 | 4.87 | 1037 | 5.69 | 1090 | 6.52 | 1141 | 7.36 | 1202 | 8.36 | 1260 | 9.38 | 1315 | 10.42
9747 | 1900 | 953 | 4.41 | 1008 | 5.25 | 1060 | 6.1 | 1110 | 6.96 | 1160 | 7.84 | 1209 | 8.75 | 1267 | 9.8 | 1322 | 10.88 | 1375 | 11.97
10260 | 2000 | 981 | 4.76 | 1032 | 5.64 | 1084 | 6.53 | 1133 | 7.43 | 1180 | 8.34 | 1227 | 9.27 | 1274 | 10.23 | 1329 | 11.34 | 1381 | 12.46 | 1432 | 13.61
11286 | 2200 | 1037 | 5.53 | 1086 | 6.49 | 1132 | 7.46 | 1180 | 8.43 | 1225 | 9.41 | 1268 | 10.41 | 1312 | 11.42 | 1354 | 12.44 | 1395 | 13.48 | 1446 | 14.7
12312 | 2400 | 1096 | 6.39 | 1142 | 7.43 | 1187 | 8.47 | 1229 | 9.53 | 1272 | 10.58 | 1314 | 11.65 | 1355 | 12.73 | 1394 | 13.82 | 1434 | 14.92 | 1473 | 16.03
13338 | 2600 | 1155 | 7.36 | 1200 | 8.46 | 1243 | 9.59 | 1284 | 10.72 | 1323 | 11.86 | 1362 | 13 | 1402 | 14.14 | 1440 | 15.3 | 1476 | 16.48 | 1512 | 17.67
14364 | 2800 | 1217 | 8.46 | 1259 | 9.61 | 1300 | 10.8 | 1340 | 12.02 | 1377 | 13.24 | 1414 | 14.46 | 1450 | 15.69 | 1487 | 16.91 | 1523 | 18.15 | 1558 | 19.4
15390 | 3000 | 1280 | 9.68 | 1320 | 10.9 | 1359 | 12.15 | 1397 | 13.43 | 1433 | 14.73 | 1469 | 16.03 | 1503 | 17.33 | 1536 | 18.65 | 1571 | 19.96 | 1605 | 21.28
16416 | 3200 | 1344 | 11.04 | 1382 | 12.32 | 1418 | 13.63 | 1455 | 14.97 | 1491 | 16.34 | 1525 | 17.72 | 1558 | 19.11 | 1591 | 20.5 | 1622 | 21.89 | 1653 | 23.3
17442 | 3400 | 1408 | 12.54 | 1445 | 13.89 | 1480 | 15.26 | 1514 | 16.66 | 1549 | 18.09 | 1582 | 19.54 | 1615 | 21.01 | 1646 | 22.49 | 1677 | 23.95 | 1707 | 25.43
18468 | 3600 | 1474 | 14.2 | 1509 | 15.61 | 1543 | 17.05 | 1576 | 18.51 | 1608 | 19.99 | 1640 | 21.51 | 1672 | 23.04 | 1703 | 24.59 | 1732 | 26.16 | 1761 | 27.71
19494 | 3800 | 1539 | 15.99 | 1574 | 17.5 | 1607 | 19 | 1638 | 20.53 | 1669 | 22.07 | 1699 | 23.64 | 1730 | 25.23 | 1760 | 26.85 | 1789 | 28.48 | 1817 | 30.13
20520 | 4000 | 1605 | 17.89 | 1639 | 19.56 | 1671 | 21.13 | 1701 | 22.71 | 1731 | 24.32 | 1760 | 25.95 | 1789 | 27.6 | 1818 | 29.28 | 1847 | 30.97 | 1874 | 32.68
21546 | 4200 | 1672 | 19.96 | 1704 | 21.79 | 1735 | 23.43 | 1765 | 25.09 | 1794 | 26.76 | 1822 | 28.45 | 1850 | 30.15 | 1877 | 31.89 | 1905 | 33.64 | 1932 | 35.42
22572 | 4400 | 1739 | 22.2 | 1770 | 24.11 | 1801 | 25.93 | 1829 | 27.65 | 1858 | 29.38 | 1885 | 31.14 | 1912 | 32.91 | 1938 | 34.7 | 1964 | 36.51 | 1990 | 38.34
23598 | 4600 | 1806 | 24.63 | 1837 | 26.61 | 1866 | 28.62 | 1894 | 30.41 | 1922 | 32.21 | 1948 | 34.02 | 1974 | 35.86 | 2000 | 37.71 | 2024 | 39.58 | 2049 | 41.4
24624 | 4800 | 1874 | 27.25 | 1903 | 29.3 | 1932 | 31.38 | 1960 | 33.38 | 1986 | 35.24 | 2012 | 37.12 | 2037 | 39.02 | 2062 | 40.93 | 2086 | 42.86 | 2110 | 44.81
25650 | 5000 | 1942 | 30.07 | 1971 | 32.2 | 1998 | 34.35 | 2025 | 36.53 | 2051 | 38.49 | 2076 | 40.44 | 2101 | 42.4 | 2125 | 44.38 | 2149 | 46.37 | 2172 | 48.37
26676 | 5200 | 2010 | 33.1 | 2038 | 35.3 | 2065 | 37.53 | 2091 | 39.78 | 2117 | 41.97 | 2141 | 43.98 | 2165 | 46 | 2189 | 48.04 | 2212 | 50.1 | 2234 | 52.17
27702 | 5400 | 2079 | 36.34 | 2106 | 38.62 | 2132 | 40.92 | 2157 | 43.24 | 2182 | 45.59 | 2206 | 47.76 | 2230 | 49.84 | 2253 | 51.95 | 2275 | 54.06 | 2297 | 56.20
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
12312 | 2400 | 1510 | 17.15 | 1600 | 19.77 | 1686 | 22.48
13338 | 2600 | 1549 | 18.85 | 1620 | 21.26 | 1700 | 23.98 | 1782 | 26.89 | 1859 | 29.85
14364 | 2800 | 1592 | 20.67 | 1660 | 23.22 | 1726 | 25.79 | 1795 | 28.57 | 1873 | 31.67 | 1947 | 34.82 | 2017 | 38.01
15390 | 3000 | 1639 | 22.6 | 1702 | 25.3 | 1765 | 38.02 | 1828 | 30.77 | 1887 | 33.55 | 1960 | 36.82 | 2031 | 40.15 | 2099 | 43.53 | 2164 | 46.95
16416 | 3200 | 1686 | 24.69 | 1749 | 27.51 | 1808 | 30.38 | 1867 | 33.27 | 1926 | 36.18 | 1983 | 39.13 | 2045 | 42.34 | 2113 | 45.85 | 2178 | 49.41 | 2241 | 53.01
17442 | 3400 | 1736 | 26.92 | 1796 | 29.88 | 1855 | 32.87 | 1911 | 35.9 | 1966 | 38.98 | 2022 | 42.05 | 2076 | 45.15 | 2128 | 48.29 | 2192 | 51.92 | 2255 | 55.65
18468 | 3600 | 1790 | 29.26 | 1845 | 32.41 | 1903 | 35.53 | 1958 |  | 2011 | 41.89 | 2063 | 45.13 | 2116 | 48.37 | 2168 | 51.63 | 2218 | 54.03 | 2260 | 58.35
19494 | 3800 | 1845 | 31.77 | 1899 | 35.04 | 1951 | 38.37 | 2006 | 41.65 | 2058 | 44.97 | 2109 | 48.34 | 2158 | 51.74 | 2207 | 55.15 | 2257 | 58.57 | 2305 | 62.02
20520 | 4000 | 1901 | 34.41 | 1954 | 37.86 | 2005 | 41.3 | 2054 | 44.8 | 2106 | 48.24 | 2156 | 51.73 | 2204 | 55.25 | 2251 | 58.81 | 2297 | 62.41 | 2345 | 65.98
21546 | 4200 | 1958 | 37.21 | 2010 | 40.83 | 2059 | 44.43 | 2107 | 48.05 | 2154 | 51.71 | 2203 | 55.32 | 2251 | 58.97 | 2297 | 62.65 | 2342 | 66.36 | 2386 | 70.11
22572 | 4400 | 2016 | 40.19 | 2066 | 43.94 | 2115 | 47.75 | 2162 | 51.5 | 2207 | 55.28 | 2252 | 59.12 | 2299 | 62.89 | 2345 | 66.69 | 2389 | 70.52 | 2432 | 74.39
23598 | 4600 | 2075 | 43.38 | 2124 | 47.25 | 2171 | 51.18 | 2217 | 55.16 | 2262 | 59.06 | 2305 | 63.01 | 2347 | 67.01 | 2392 | 70.94 | 2436 | 74.9 | 2479 | 78.89
24624 | 4800 | 2134 | 46.77 | 2182 | 50.77 | 2228 | 54.82 | 2273 | 58.93 | 2317 | 63.09 | 2360 | 67.12 | 2401 | 71.24 | 2441 | 75.39 | 2484 | 79.5
25650 | 5000 | 2195 | 50.4 | 2240 | 54.5 | 2286 | 58.67 | 2330 | 62.9 | 2373 | 67.18 | 2414 | 71.47 | 2455 | 75.7 | 2495 | 79.97