## Sheet1
AIRFOIL BLADE
SIZE S - AF - 37 | [6 empty] | SINGLE WIDTH |  |  |  |  | MAXIMUM CLASS OPERATING RPM
[7 empty] | SINGLE INLET |  |  |  |  | FAN TEMPERATURE
Wheel Diameter 36 ½inches 927 mm | [13 empty] | SIZE 37 |  | ₋20˚ to 150˚ F ₋29˚ to 66˚C
Wheel circumference 9.56 feet 2.914 m | [13 empty] | CLASS I |  | 1129
Inlet Diameter / Area 39 3/16 inches Dia/8.30 sq f.t 995mm /.7711 m² | [13 empty] | CLASS II |  | 1473
Outlet Size Area 38 ⅜*28 ⅝ Inches I.D/7.63 sq.ft 975*727mm/.7088m² | [13 empty] | CLASS III |  | 1855
Tip Speed 9.56 * rpm ft./minute 2.914*RPM m/minute | [13 empty] | CLASS IV |  | 2041
Maximum BHP 13.04*(RPM÷1000)³ BHP 9.724* (RPM ÷1000)³ KW
VOL | OUT | ¼" SP |  | ⅜" SP |  | ½" SP |  | ⅝" SP |  | 3/4" SP |  | ⅞" SP |  | 1" SP |  | 1 ¼" SP |  | 1 ½" SP |  | 1 3/4" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
4578 | 600 | 264 | 0.24 | 298 | 0.34 | 335 | 0.45
5341 | 700 | 285 | 0.29 | 317 | 0.41 | 345 | 0.53 | 377 | 0.65 | 407 | 0.79
6104 | 800 | 306 | 0.35 | 337 | 0.49 | 364 | 0.62 | 389 | 0.75 | 415 | 0.9 | 443 | 1.05 | 469 | 1.2
6867 | 900 | 329 | 0.43 | 357 | 0.57 | 384 | 0.73 | 408 | 0.88 | 431 | 1.02 | 452 | 1.18 | 478 | 1.34 | 525 | 1.69
7630 | 1000 | 354 | 0.52 | 379 | 0.67 | 404 | 0.84 | 428 | 1.01 | 450 | 1.17 | 471 | 1.34 | 490 | 1 | 533 | 1.86 | 576 | 2.24
8393 | 1100 | 379 | 0.62 | 402 | 0.79 | 426 | 0.96 | 448 | 1.14 | 470 | 1.33 | 490 | 1.51 | 509 | 1.69 | 544 | 2.06 | 585 | 2.46 | 624 | 2.88
9156 | 1200 | 405 | 0.75 | 427 | 0.92 | 447 | 1.1 | 469 | 1.3 | 490 | 1.49 | 510 | 1.7 | 528 | 1.9 | 563 | 2.29 | 595 | 2.7 | 632 | 3.13
9919 | 1300 | 431 | 0.88 | 452 | 1.07 | 472 | 1.26 | 491 | 1.46 | 511 | 1.67 | 530 | 1.89 | 548 | 2.11 | 582 | 2.54 | 614 | 2.97 | 644 | 3.41
10682 | 1400 | 458 | 1.04 | 478 | 1.24 | 497 | 1.44 | 514 | 1.65 | 532 | 1.87 | 551 | 2.1 | 569 | 2.33 | 602 | 2.81 | 633 | 3.27 | 662 | 3.73
11445 | 1500 | 485 | 1.21 | 504 | 1.43 | 522 | 1.64 | 539 | 1.87 | 555 | 2.09 | 572 | 2.33 | 590 | 2.57 | 622 | 3.08 | 653 | 3.59 | 682 | 4.07
12208 | 1600 | 512 | 1.4 | 530 | 1.64 | 548 | 1.87 | 564 | 2.1 | 580 | 2.34 | 595 | 2.58 | 611 | 2.84 | 643 | 3.36 | 673 | 3.9 | 701 | 4.45
12971 | 1700 | 539 | 1.61 | 557 | 1.88 | 574 | 2.12 | 590 | 2.36 | 605 | 2.61 | 619 | 2.86 | 633 | 3.12 | 664 | 3.67 | 693 | 4.23 | 721 | 4.81
13734 | 1800 | 567 | 1.85 | 584 | 2.13 | 600 | 2.39 | 615 | 2.64 | 630 | 2.9 | 644 | 3.17 | 658 | 3.44 | 686 | 4 | 714 | 4.59 | 741 | 5.19
14497 | 1900 | 594 | 2.11 | 611 | 2.4 | 626 | 2.68 | 641 | 2.95 | 655 | 3.23 | 669 | 3.5 | 682 | 3.79 | 708 | 4.36 | 735 | 4.97 | 762 | 0.59
15260 | 2000 | 622 | 2.39 | 638 | 2.7 | 653 | 3.01 | 667 | 3.29 | 681 | 3.58 | 695 | 3.86 | 707 | 4.16 | 732 | 4.76 | 757 | 5.38 | 783 | 6.02
16786 | 2200 | 678 | 3.04 | 693 | 3.38 | 707 | 3.72 | 720 | 4.06 | 733 | 4.36 | 746 | 4.68 | 758 | 4.99 | 782 | 5.64 | 804 | 6.29 | 726 | 6.97
18312 | 2400 | 734 | 3.82 | 748 | 4.18 | 761 | 4.54 | 774 | 4.91 | 786 | 5.28 | 798 | 5.62 | 810 | 5.96 | 832 | 6.65 | 854 | 7.35 | 874 | 8.07
19838 | 2600 | 791 | 4.72 | 804 | 5.11 | 816 | 5.5 | 828 | 5.9 | 840 | 6.3 | 851 | 6.7 | 862 | 7.06 | 884 | 7.8 | 904 | 8.55 | 924 | 9.31
21364 | 2800 | 848 | 5.76 | 860 | 6.17 | 872 | 6.6 | 883 | 7.02 | 874 | 7.54 | 905 | 7.89 | 916 | 8.32 | 936 | 9.1 | 955 | 9.9 | 974 | 10.71
22890 | 3000 | 905 | 6.95 | 917 | 7.4 | 92 | 7.84 | 938 | 8.3 | 949 | 8.75 | 959 | 9.21 | 969 | 6.68 | 989 | 10.57 | 1007 | 11.41 | 1025 | 12.27
24416 | 3200 | 963 | 8.31 | 973 | 8.78 | 984 | 9.25 | 994 | 9.73 | 1004 | 10.22 | 1014 | 10.71 | 1023 | 11.2 | 1042 | 12.19 | 1060 | 13.1 | 1077 | 14
25942 | 3400 | 1020 | 9.83 | 1030 | 10.33 | 1040 | 10.84 | 1050 | 11.34 | 1059 | 11.86 | 1069 | 12.37 | 1078 | 12.89 | 1096 | 13.94 | 1113 | 14.98 | 1130 | 15.93
27468 | 3600 | 1078 | 11.55 | 1087 | 12.07 | 1097 | 12.6 | 1106 | 13.14 | 1115 | 13.68 | 1124 | 14.22 | 1133 | 14.77 | 1150 | 15.87 | 1166 | 16.98 | 1183 | 18.05
28994 | 3800 | 1136 | 13.45 | 1145 | 14.01 | 1154 | 14.56 | 1162 | 15.13 | 1171 | 15.69 | 1179 | 16.26 | 1188 | 16.84 | 1204 | 17.99 | 1220 | 19.16 | 1236 | 20.34
VOL | OUT | 2" SP |  | 2 ½" SP |  | 3" SP |  | 3 ½" SP |  | 4" SP |  | 4 ½" SP |  | 5" SP |  | 5 ½" SP |  | 6 " SP |  | 6 ½" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
10682 | 1400 | 690 | 4.2 | 752 | 5.22 | 812 | 6.28
11445 | 1500 | 709 | 4.57 | 761 | 5.59 | 821 | 6.71 | 876 | 7.85
12208 | 1600 | 728 | 4.96 | 778 | 6.02 | 830 | 7.15 | 885 | 8.35 | 936 | 9.57
12971 | 1700 | 747 | 5.39 | 796 | 6.49 | 842 | 7.63 | 894 | 8.86 | 945 | 10.13 | 993 | 11.43
13734 | 1800 | 767 | 5.81 | 816 | 6.9 | 860 | 8.17 | 903 | 9.39 | 954 | 10.72 | 1002 | 12.07 | 1047 | 13.44
14497 | 1900 | 787 | 6.23 | 835 | 7.52 | 879 | 8.75 | 921 | 10.01 | 962 | 11.32 | 1010 | 12.72 | 1056 | 14.15 | 1099 | 15.59
15260 | 2000 | 808 | 6.69 | 855 | 8.05 | 899 | 9.36 | 940 | 10.66 | 978 | 11.99 | 1019 | 13.39 | 1065 | 14.87 | 1108 | 16.37 | 1149 | 17.89
16786 | 2200 | 850 | 7.68 | 896 | 9.13 | 938 | 10.63 | 978 | 12.08 | 1016 | 13.5 | 1052 | 14.95 | 1086 | 16.43 | 1125 | 17.99 | 1166 | 19.61 | 1206 | 21.26
18312 | 2400 | 894 | 8.8 | 938 | 10.34 | 979 | 11.93 | 1018 | 13.56 | 1055 | 15.16 | 1090 | 16.7 | 1124 | 18.27 | 1156 | 19.86 | 1188 | 21.47 | 1223 | 23.17
19838 | 2600 | 943 | 10.08 | 980 | 11.68 | 1021 | 13.36 | 105 | 15.09 | 1094 | 16.85 | 1129 | 18.63 | 1162 | 20.28 | 1194 | 21.96 | 1225 | 23.66 | 1255 | 25.38
21364 | 2800 | 992 | 11.53 | 1027 | 13.2 | 1063 | 14.94 | 1100 | 16.76 | 1135 | 18.61 | 1169 | 20.5 | 1201 | 22.43 | 1233 | 24.24 | 1263 | 26.03 | 1292 | 27.84
22890 | 3000 | 1043 | 13.13 | 1077 | 14.9 | 1109 | 16.7 | 1143 | 18.59 | 1177 | 20.53 | 1210 | 22.51 | 1242 | 24.52 | 1272 | 26.57 | 1302 | 28.6 | 1331 | 30.5
24416 | 3200 | 1094 | 14.92 | 1127 | 16.77 | 1158 | 18.66 | 1187 | 20.6 | 1220 | 22.62 | 1252 | 24.69 | 1283 | 26.79 | 1313 | 28.92 | 1342 | 31.09 | 1370 | 33.29
25942 | 3400 | 1146 | 16.88 | 1177 | 18.83 | 1207 | 20.82 | 1236 | 22.84 | 1263 | 24.89 | 1294 | 27.04 | 1325 | 29.24 | 1354 | 31.46 | 1383 | 33.71 | 1410 | 36
27468 | 3600 | 1198 | 19.05 | 1229 | 21.09 | 1258 | 23.17 | 1285 | 25.28 | 1312 | 27.42 | 1338 | 29.6 | 1367 | 31.88 | 1396 | 34.19 | 1424 | 36.53 | 1451 | 38.91
28994 | 3800 | 1251 | 21.43 | 1280 | 23.56 | 1308 | 25.73 | 1335 | 27.93 | 1362 | 30.16 | 1387 | 32.43 | 1411 | 34.73 | 1439 | 37.12 | 1466 | 39.55 | 1493 | 42.01
30520 | 4000 | 1304 | 24.03 | 1333 | 26.26 | 1360 | 28.51 | 1386 | 30.81 | 1411 | 33.13 | 1436 | 35.48 | 1460 | 37.87 | 1483 | 40.28 | 1509 | 42.79 | 1535 | 45.34
32046 | 4200 | 1358 | 26.73 | 1438 | 29.18 | 1412 | 31.53 | 1437 | 33.92 | 1462 | 36.33 | 1486 | 38.77 | 1509 | 41.25 | 1532 | 43.75 | 1554 | 46.28 | 1578 | 48.88
33572 | 4400 | 1412 | 29.66 | 1385 | 32.35 | 1464 | 34.8 | 1489 | 37.27 | 1513 | 39.78 | 1536 | 42.31 | 1559 | 44.87 | 1581 | 47.46 | 1602 | 50.07 | 1624 | 52.72
35098 | 4600 | 1466 | 32.83 | 1492 | 35.67 | 1517 | 38.31 | 1541 | 40.88 | 1564 | 43.48 | 1587 | 46.1 | 1609 | 48.75 | 1631 | 51.43 | 1652 | 54.13 | 1672 | 56.86
36624 | 4800 | 1520 | 36.25 | 1545 | 39.2 | 1570 | 42.1 | 1593 | 44.76 | 1616 | 47.45 | 1638 | 50.16 | 1660 | 52.9 | 1681 | 55.67 | 1701 | 58.46 | 1721 | 61.27
38150 | 5000 | 1575 | 39.92 | 1599 | 42.98 | 1623 | 46.07 | 1646 | 48.92 | 1668 | 51.7 | 1689 | 54.5 | 1711 | 57.33 | 731 | 60.19 | 1751 | 63.07 | 1771 | 65.97
39676 | 5200 | 1630 | 43.87 | 1654 | 47.03 | 1677 | 50.22 | 1699 | 53.36 | 1720 | 56.24 | 1741 | 59.13 | 1762 | 62.05 | 1782 | 65 | 1802 | 67.96 | 1821 | 70.96
41202 | 5400 | 1685 | 48.10 | 1708 | 51.36 | 1730 | 54.66 | 1752 | 57.99 | 1773 | 61.08 | 1794 | 64.06 | 1814 | 67.07 | 1833 | 70.11 | 1853 | 73.17 | 1871 | 76.25
VOL | OUT | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP
CFM | VEL | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P. | R.P.M. | B.H.P.
18312 | 2400 | 1261 | 29.94 | 1333 | 28.52 | 1401 | 32.16
19838 | 2600 | 1283 | 27.12 | 1351 | 30.85 | 1418 | 37.7 | 1482 | 38.62
21364 | 2800 | 1321 | 29.67 | 1375 | 33.4 | 1436 | 37.35 | 1499 | 41.47 | 1560 | 45.65 | 1618 | 49.88
22890 | 3000 | 1359 | 32.42 | 1412 | 36.32 | 1463 | 40.29 | 1517 | 44.44 | 1577 | 48.82 | 1635 | 53.26 | 1690 | 57.74 | 1744 | 62.28
24416 | 3200 | 1397 | 35.38 | 1450 | 39.45 | 1500 | 43.6 | 1548 | 47.82 | 1595 | 52.12 | 1652 | 56.76 | 1708 | 61.45 | 1761 | 66.19 | 1812 | 70.98 | 1862 | 75.81
25942 | 3400 | 1437 | 38.31 | 1489 | 42.82 | 1538 | 47.14 | 1586 | 51.53 | 1631 | 55.99 | 1675 | 60.51 | 1725 | 65.29 | 1778 | 70.24 | 1829 | 75.23 | 1879 | 80.26
27468 | 3600 | 1478 | 41.31 | 1528 | 46.19 | 1577 | 50.91 | 1624 | 55.48 | 1669 | 60.11 | 1712 | 64.8 | 1753 | 69.55 | 1796 | 74.42 | 1847 | 79.61 | 1896 | 84.85
2894 | 3800 | 1519 | 44.5 | 1569 | 49.56 | 1616 | 54.73 | 1662 | 59.68 | 1707 | 64.49 | 1749 | 69.35 | 1790 | 74.27 | 1830 | 79.25 | 1869 | 84.28 | 1913 | 89.59
30520 | 4000 | 1561 | 47.92 | 1610 | 53.15 | 1657 | 58.49 | 1701 | 63.92 | 1745 | 69.13 | 1787 | 74.17 | 1828 | 79.26 | 1867 | 84.41 | 1906 | 89.61 | 1943 | 94.87
32046 | 4200 | 1603 | 51.55 | 1651 | 56.96 | 1698 | 62.47 | 1742 | 68.08 | 1784 | 73.78 | 1826 | 79.26 | 1866 | 84.53 | 1905 | 89.85 | 1943 | 95.22 | 1980 | 100.65
33572 | 4400 | 1646 | 55.42 | 1693 | 61.01 | 1739 | 66.7 | 1783 | 72.47 | 1825 | 78.34 | 1865 | 84.3 | 1905 | 90.09 | 1943 | 95.58 | 1981 | 101.13 | 2017 | 106.72
35098 | 4600 | 1692 | 59.62 | 1736 | 65.3 | 1781 | 71.17 | 1824 | 77.12 | 1865 | 83.16 | 1905 | 89.28 | 1944 | 95.49 | 1982 | 101.62 | 2019 | 107.34
36624 | 4800 | 1741 | 64.12 | 1779 | 69.87 | 1823 | 75.89 | 1866 | 82.02 | 1906 | 88.23 | 1946 | 94.53 | 1984 | 100.91 | 2021 | 107.36
38150 | 5000 | 1790 | 68.9 | 1828 | 74.82 | 1866 | 80.88 | 1908 | 87.19 | 1948 | 93.58 | 1987 | 100.05 | 2025 | 106.59